## Com.ECC - Envelope
2020 NYCECC Tabular Analysis Commercial Building in compliance with ECC
Energy Code Scope of Work
For all ALTERATION job applications where the proposed scope of alteration work is limited to partial areas of the existing buildings and/or conditions, please provide a detailed description of the proposed scope of work here, and itemize the altered elements in the tabular format below.
Note for ALTERATION job application: For each altered element where ALTERATION-specific exception/allowance is applied, create a row in the table to cite the applicable code section and to report the Supporting Documentation location. For examples of ALTERATION-specific exceptions/allowances, refer to 101.2.5, C503.1, C503.6, and C504.2.
NYCECC Citation | Provision | Item Description | Code Prescriptive Value (ECC) | Proposed Design Value | Supporting Documentation
C401.2.1 | Application to Group R-3 buildings, Permanent Certificate | Permanent certificate posted on the electrical distribution panel. | A permanent certificate shall be completed by the builder or registered design professional and posted on the wall in the space where the furnace is located, a utility room or an approved location inside the building. The certificate shall stateinsulation R-values, U-factors and the solar heat gain coefficient (SHGC) of fenestration, results from any required duct system and building envelope air leakage testing done on the building, and equipment efficiencies. When located on an electrical panel the certificate shall not cover or obstruct the visibility of any required labels. | Sample text: Certificate provided as per code requirements. | Sample text: See architectural plans, A-XXX, A-XXX and specifications drawing A-XXX
C401.2.1 | Application to Group R-3 buildings, air leakage testing | Air leakage testing statement | Less than 3 ACH. A written report of the test results shall be prepared and signed by the party conducting the test and provided to the code official and shall include the items listed in R402.4.1.2. | Sample text: Building thermal envelope to be tested to no more than 3 ACH @ 50 PA and witnessed by the Progress Inspector as indicated on TR-8 inspection IA7. | Sample text: EN-XXX notes
C401.2.1 | Application to Group R-3 buildings, HRV/ERV or balanced ventilation | Balanced ventilation or ventilation system equipped with HRV/ERV system | Sample text: Balanced ventilation system design: Dwelling unit floor area (2400 sq ft), 4 bedrooms = 75 cfm continuous airflow Run-time percentage: 50%, Factor = 2 Total airflow = 75 cfm * 2 = 150 cfm Boiler heating system = 58 W/CFM fan efficacy ( minimum) | Sample text: Two bathroom exhaust fans @ 50 cfm each Kitchen exhaust fan @ 75 cfm Outdoor air flow through air handler = 150 cfm Fan efficacy= 58 W/CFM | Sample text: M-XXX (Details), M-XXX (Schedule, M-XXX (Floor plans)
C402.1.3, C402.2, Tables C402.1.3, C402.1.4 | Roof Assembly - Insulation entirely above roof deck | Sample text: New steel-deck roof | Minimum R-33ci | Sample text: Roof Type 1: 7” XPS (R -35) continuous insulation above deck | Sample text: Roof Type 1: A-XXX (Roof Plan) A-XXX (Wall Sections) X-Y/A-XXY (Roof Details)
Tables C402.1.3, Table C402.1.4, Section C402.2 | Roof assembly - metal buildings | Sample text: New roof on metal building | Sample text: Minimum R-19 + R-11 LS | Sample text: Roof Type 1: R-19 fiberglass batt cavity insulation plus 3" EPS (R-12) linear system (LS) with continuous insulation (ci) installed below the purlins | Sample text: Roof Type 1: A-XXX (Roof Plan) A-XXX (Wall Sections) X-Y/A-XXY (Roof Details)
Tables C402.1.3, C402.1.4 or Section C402.2 | Roof assembly - attic and other | Sample text: New attic | Sample text: Minimum R-53 | Sample text: Roof Type 1: R -53 | Sample text: Roof Type 1: A-XXX (Roof Plan) A-XXX (Wall Sections) X-Y/A-XXY (Roof Details)
Tables C402.1.3, C402.1.4 or Section C402.2 | Walls, above-grade: Mass | Sample text: 8" CMU wall with continuous rigid insulation and brick veneer. | Sample text: Minimum R-13.25ci | Sample text: 3" Extruded polystyrene (XPS) = R-15 ci | Sample text: Exterior Wall Type X: A-XXX (1st Floor Plan) 2/A-XXX (Wall Details)
Tables C402.1.3, C402.1.4 or Section C402.2 | Walls, above-grade: Metal framed | Sample text: Steel-framed wall, 2x4 framing 16" O.C | Sample text: Minimum R-13 + R-8.5ci | Sample text: R-13 batt insulation installed between framing + R-10 ci installed on the exterior of the building | Sample text: Exterior Wall Type X: A-XXX (1st Floor Plan) 2/A-XXX (Wall Details)
Tables C402.1.3, C402.1.4 or Section C402.2 | Walls, above-grade: Wood framed & other | Sample text: Above-grade wood-framed wall 2x4 framing, 16" o.c. | Sample text: Minimum R-13 + R-4.5ci or R-19 + R-1.5ci | Sample text: Exterior Wall Type 1: R-13 fiberglass batt cavity insulation + 2" EPS (R-8) ci | Sample text: Exterior Wall Type X: A-XXX (1st Floor Plan) 2/A-XXX (Wall Details)
Tables C402.1.3, C402.1.4 or Section C402.2 | Below-grade walls | Sample text: Thermal insulation on the interior of new basement wall. | Sample text: Minimum R-10ci | Sample text: 2" Extruded Polystyrene (XPS) = R-10 | Sample text: Exterior Wall Type X: A-XXX (Basement Floor Plan) 2/A-XXX (Foundation Details)
Tables C402.1.3, C402.1.4 or Section C402.2 | Floors: Mass | Sample text: Thermal insulation at new concrete floor over garage. | Sample text: Minimum R-16.7ci | Sample text: 3.5" Extruded Polystyrene (XPS) = R-17.5 ci | Sample text: Exterior Wall Type X: A-XXX (Basement Floor Plan) 2/A-XXX (Foundation Details)
Tables C402.1.3, C402.1.4 or Section C402.2 | Floors: Joist/framing | Sample text: Thermal insulation at new steel-joist floor over unconditioned space. | Sample text: Minimum R-30 | Sample text: Exterior Wall Type 1: R-49 fiberglass batt cavity insulation | Sample text: Exterior Wall Type X: A-XXX (Basement Floor Plan) 2/A-XXX (Foundation Details)
Tables C402.1.3, C402.1.4 or Section C402.2 | Slab-on-grade floors: Heated slabs | Sample text: Slab-on-grade with radiant heating. | Sample text: Minimum R-15 for 24"below plus R-5ci under full slab | Sample text: R-5ci under full slab, R-15 extending from the top of the footing to 24" below | Sample text: Exterior Wall Type X: A-XXX (Basement Floor Plan) 2/A-XXX (Foundation Details)
Tables C402.1.3, C402.1.4 or Section C402.2 | Opaque doors, Nonswinging | Sample text: Insulated metal roll-up garage door. | Sample text: Minimum R-4.75 | Sample text: R-5 | Insulated Metal Roll-up Door: A-301-302 (Elevations) A-501 (Schedules)
C402.1.1 | Low-energy buildings | Sample text: Low-energy building thermal envelope exemption | The following shall be exempt from the building thermal envelope provisions of Section C402: peak design rate of energy usage less than 3.4 Btu/h ● ft2 for space conditioning purposes. | Sample text: 10,000 SF Garage, Total heating capacity = 30,000 BTU/h Total cooling capacity = none Peak design rate = 3.0 BTU/h● ft2 | Sample text: A-XXX, A-XX1-XX2 (Building Elevations) A-5XX (Schedules) A-6XX (Section details)
C402.1.4 Tables C402.1.3, C402.1.4 | Assembly U-factor, C-factor or F-factor-based method | Sample text: 8" block wall with R-13 batt insulation in metal studs and R-10 continuous exterior insulation | Sample text: Mass wall U = 0.086 | Sample text: U-factor calculated using ASHRAE 90.1-2016 Appendix A Ru - 2.07 (Table A3.1-3, 8" block, 115#) R - 10.5 (Table A3.1-4, 10ci) R - 4.7 (Table A3.1-4, R-13 in 3.5 metal stud) U = 1/(2.07 + 10.5 + 4.7) = 0.058 | Sample text: A-XXX, A-XX1-XX2 (Building Elevations) A-5XX (Schedules) A-6XX (Section details)
C402.2.1 | Multiple layers of continuous insulation | Sample text: Installation of multiple layers of continuous insulation. | Two or more insulation boards in construction assemblies shall be in accordance with Section C303.2. If the manufacturer does not call for multiple layers the edge joints between each layer of continuous insulation boards shall be staggered. | Sample text: Stagger the edge joints between each layer of continuous insulation boards. | Sample text: A-XX1-XX2 (Building Elevations) A-5XX (Schedules) A-6XX (Section details)
C402.2.8 | Fireplaces | Sample text: Factory built gas-fired fireplace | New fireplaces shall be listed and labeled with tight-fitting doors | Sample text: Factory built fireplace listed/labeled UL 127 with tight-fitting doors | Sample text: A-XXX, specs
C402.2.9 | Continuous insulation | Parapet design | Parapet shall be wrapped with continuous insulation having minimum R-value equivalent to the adjacent wall assembly. Above-grade wall assembly - 10ci. | Parapet wrapped in R-10ci | Sample text: A-XXX,
C402.4, Table C402.4 | Fenestration (Prescriptive) | Sample text: Fenestration requirements Elevation showing 95' demarcation | Sample text: Window U-factor below 95 feet Umax-0.30 (fixed) Umax-0.40 (operable) Window U-factor above 95 feet Umax-0.36 (fixed) Umax-0.42 (operable) SHGCmax - 0.36 | Sample text: W-1 (fixed) - installed below 95 feet U-0.28, SHGC - 0.36 W-2 (operable) - installed below 95 feet U-0.40, SHGC - 0.36 W-3 (fixed) - installed 95 feet & above U-0.32, SHGC - 0.36 W-2 (operable) - installed 95 feet & above U-0.40, SHGC - 0.36 | Sample text: A-XXX, EN-XXX (elevation showing 95' demarcation)
C402.4.1 | Maximum area | Sample text: Window to wall Ratio | Sample text: 30% Maximum | Sample text: 25% | Sample text: A-XX1-XX2 (Building Elevations) Gross wall area and gross window area.
C402.4.1.1 | Increased vertical fenestration area with daylight responsive controls | Sample text: Increased Window to wall Ratio with daylighting controls | Sample text: 40% Maximum, >25% of conditioned floor area is in daylight zone. | Sample text: WWR = 35%, 30% of conditioned floor area is in daylight zone, automatic daylight controls installed, VT>0.396 | Sample text: A-XX1-XX2 (Building Elevations) Gross wall area and gross window area. A-XXX (daylight zone calculation). A-XX (window schedule showing VT). E-XXX (Lighting fixture schedules)
C402.4.1.2 | Increased skylight area with daylight responsive controls | Sample text: Roof area to skylight ratio | Sample text: 3% Maximum | Sample text: 2.2% | Sample text: Horizontal fenestration: A-1XX (Roof Plan) A-5XX (Schedules) A-6XX (Section details)
C402.4.2 | Minimum skylight fenestration area | Minimum skylight requirements | Sample text: Total daylight zone under skylights shall be not less than half the floor area. Skylights in office, storage, automotive service, manufacturing, nonrefrigerated warehouse, retail store and distribution/sorting area: Haze factor greater than 90%. | Sample text: Skylights provided on FL-12 above corridors and offices Haze factor 92% for all skylights. | Sample text: A-XXX (daylight zone calculation)
C402.5 | Air leakage-thermal envelope (Mandatory) | Sample text: Air leakage-thermal envelope | The thermal envelope of the building must comply with Sections C402.5.1 through C402.5.8. Pressure differential of 0.3 inch water gauge. Air leakage rate 0.40 cfm/ft2maximum. Must comply with Sections C402.5.5, C402.5.6, and C402.5.7. | Sample text: Building thermal envelope to be tested to no more than 0.4 cfm/ft2 of envelope area @ 75 PA and witnessed by the Progress Inspector as indicated on TR-8 inspection IIA7. | Sample text: Notes (A-XXX) Specs (A-XXX)
C402.5.1 | Air barriers | Sample text: Air barrier material | A continuous air barrier for the opaque buildings envelope shall comply with Section C402.5.1.2.1 or C402.5.1.2.2. | Sample text: Continuous air barrier - 1/2 inch XPS with all joints sealed according to mfg.'s instructions. | Sample text: Air sealing notes (A-XXX)
C402.5.1.2.1 | Materials | Sample text: Materials | Items 1 through 15 listed in this section must comply with the requirements of this section. | Sample text: Plywood with a thickness of not less than 3/8 inch meet the requirements of Section C402.5.1.2.1. | Sample text: Notes (A-XXX) Specs (A-XXX)
C402.5.1.2.2 | Assemblies | Sample text: Assemblies | Items 1 through 3 listed in this section must comply with the requirements of this section. | Sample text: Concrete masonry walls coated with either one application of block filler or two applications of a sealer coating meet the requirements of C402.5.1.2.2, provided joints are sealed and the requirements of Section C402.5.1.1 are met. | Sample text: Notes (A-XXX) Specs (A-XXX)
C402.5.1.3 | Air barrier testing | Sample text: Air barrier testing | New buildings 10,000 to 50,000 square feet, and less than or equal to 75 feet in height must show compliance through testing. | Sample text: All air barrier testing to be in accordance with ASTM E 779. | Sample text: Air testing notes (A-XXX)
C402.5.2, Table C402.5.2 | Air leakage of fenestration | Sample text: Replace curtainwall and glazed entrance doors, Floor 1. | Max Air Leakage Rates: Curtain walls and storefront glazing = 0.06 cfm/sf Commercial glazed swinging entrance doors and revolving doors = 1.0 cfm/sf of door area | Sample text: Curtain walls and storefront glazing = 0.06 cfm/sf Commercial glazed swinging entrance doors and revolving doors = 1.0 cfm/sf of door area | Sample text: Vertical fenestration: A-XX1-XX2 (Building Elevations) A-5XX (Schedules) A-6XX (Section details)
C402.5.3, Tables C402.1.3, C402.1.4 | Rooms containing fuel-burning appliances | Sample text: Rooms containing fuel-burning appliances | Sample text: Direct vent appliances are exempt from the requirement. | Sample text: Boiler B-1 is direct vent SWH-1 is direct vent | Sample text: Vertical fenestration: A-XX1-XX2 (Building Elevations) A-5XX (Schedules) A-6XX (Section details)
C402.5.4 | Doors and access openings to shafts, chutes, stairways, and elevator lobbies | Sample text: Doors from corridor to stairwell A & stairwell B | Access openings from conditioned space to shafts, chutes, stairways and elevator lobbies shall meet C402.5.2 or be gasketed, weatherstripped, or sealed. | Sample text: All doors from corridor to stairway to be gasketed, weatherstripped or sealed. | Sample text: See note in general notes (A-XX1).
C402.5.5 | Air intakes, exhaust openings, stairways and shafts | Sample text: Air intakes, exhaust openings, stairways and shafts requirements for dampers | Dampers must be provided in accordance with Section C403.2.4.3. | Sample text: Stairway enclosure dampers as required. | Sample text: A-XXX Plans, M-XXX Mechanical plans
C402.5.6 | Loading dock weatherseals | Provide weatherseals at loading dock. | Cargo doors and loading dock doors shall be equipped with weatherseals to restrict infiltration when vehicles are parked in doorway. | Sample text: weatherseals provided at loading dock door. | Sample text: See note in general notes (A-XX1).
C402.5.7 | Vestibules | Sample text: Building Entrance vestibule | Vestibule provided at door separating conditioned space from the exterior. | Sample text: New 10’ deep vestibule @ building entrance. Two sets of swinging doors with self-closers. | Sample text: A-XXX (1st Floor Plan) A-5XX (Schedules) Incl. door closer notes in Comments column of Door Schedule).
C402.5.8 | Recessed lighting | Sample text: Recessed luminaires in the thermal envelope to be weather sealed. | Sample text: Recessed luminaires installed in the building thermal envelope shall be sealed to maximum air leakage 2 cfm. | Sample text: Recessed luminaires in the roof ceiling assembly sealed to 1 cfm air movement. | Sample text: A-XXX (Reflected ceiling plan) A-5XX (Schedules) Sealant notes in Comments column of Luminaire schedule.
C402.6 | Thermal bridges (Mandatory) | Thermal bridges | Clear-field thermal bridges are identified on drawings and pre-calculated assembly values are from ASHRAE 90.1 Appendix A. Point thermal bridges greater than 8in2 are identified. Linear thermal bridges are outlined in tabular format including each linear thermal bridge type, the aggregate length for each, the relevant detail and cross-section through each thermal bridge, and the Psi-value for each thermal bridge. | Clear-field thermal bridges: all wall, roof and floor assemblies are derived from Appendix A of ASHRAE 90.1 Point thermal bridges: no point thermal bridges are in this design Linear thermal bridges: See Table 1 on sheet EN-3 | Sample text: See EN-3 for tabular format of linear thermal bridges, A-XXX, A-XXX and specifications drawing A-XXX

## Com.ECC - HVAC
2020 NYCECC Tabular Analysis Commercial Building in compliance with ECC
Energy Code Scope of Work
For all ALTERATION job applications where the proposed scope of alteration work is limited to partial areas of the existing buildings and/or conditions, please provide a detailed description of the proposed scope of work here, and itemize the altered elements in the tabular format below.
Note for ALTERATION job application: For each altered element where ALTERATION-specific exception/allowance is applied, create a row in the table to cite the applicable code section and to report the Supporting Documentation location. For examples of ALTERATION-specific exceptions/allowances, refer to 101.2.5, C503.1, C503.6, and C504.2.
NYCECC Citation | Provision | Item Description | Code Prescriptive Value (ECC) | Proposed Design Value | Supporting Documentation
C403.1.1 | Calculation of heating and cooling loads (Mandatory) | Load calculations for HVAC systems | Sample text: Determined in accordance with ANSI/ASHRAE/ACCA Standard 183 HVAC Systems and Equipment Handbook | Sample text: Design loads are determined in accordance with the procedures described in the ANSI/ASHRAE/ACCA Standard183. | Signed and sealed statement from Engineer certifying compliance with Energy Code
C403.2.1 | Zone isolation required (Mandatory) | Sample text: Zone isolation | HVAC systems serving zones that are over 25,000 ft2 in floor area or that span more than one floor and are designed to operate or be occupied nonsimultaneously shall be controlled independently and divided into isolation areas where each area has isolation devices and controls configured to automatically shut off the supply of conditioned and outdoor air to and exhaust air from the isolation area. | Sample text: There are independent controls for each open floor office as specified as Zone 1 and Zone 2 | Sample text: See mechanical plans, M-XX1, M-XX2, M-XX3, mechanical control sequences, drawing M-4XX
C403.2.2 | Ventilation (Mandatory) | Sample text: Ventilation cfm and Outdoor air control | Where mechanical ventilation is provided, systems shall be capable of reducing outdoor air to the minimum requirements from Chapter 4 of the NYC MC | Sample text: Motorized dampers shall have ability to operate at minimum required ventilation rates, per requirements - list minimum CFM per space type | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
C403.3.1 | Equipment sizing (Mandatory) | HVAC systems sizing based on load calculations | Heating and cooling equipment shall not exceed calculated loads | Sample text: Specified equipment sized within load calculation limits | Signed and sealed statement from Engineer certifying compliance with Energy Code
Table C403.3.2(1) | Minimum efficiency requirements: electrically operated unitary air conditioners and condensing units | Sample text: (1) Split System 7.5 ton air cooled AC unit, AC-1 Sample text: (1) new air cooled condensing unit, 150,000 Btu/, C-1 | Sample text: 11.2 EER , 12.9 IEER (AC-1) Sample text: 10.5 EER, 11.8 IEER (C-1) | Sample text: 12.0 EER, 13.5 IEER (AC-1) Sample text: 11.1 EER, 12.2 IPLV (C-1) | Sample text: Split System AC units schedule, drawing M-XXX Sample text: Condensing units schedule, drawing M-XXX
TABLE C403.3.2(2) | Minimum efficiency requirements: electrically operated unitary and applied heat pumps | Sample text: PTAC (Cooling Mode) New construction, 12,000 BTU/h, PTAC-1 | Sample text: 14.0 - (0.300 x Cap/1000) = 10.4 EER | Sample text: 10.5 EER | Sample text: PTAC AC units schedule, drawing M-XXX
TABLE C403.3.2(3) | Minimum efficiency requirements: electrically operated PTACs, PTHPs, Single-package vertical AC, Single-package vertical HP, Room AC, and Room AC-HPs | Sample text: Room AC w/ louvered slides, 8,000 BTU/h, RAC-1 | Sample text: 10.9 CEER | Sample text: 10.9 CEER | Sample text: Room AC units schedule, drawing M-XXX
TABLE C403.3.2(4) | Warm-air furnaces and combination warm-air furnaces/air-conditioning units, warm-air duct furnaces and unit heaters, minimum efficiency requirements | Sample text: new warm-air furnace, gas fired 250,000 BTU/h, RTU-1 | Sample text: 80% Et | Sample text: 81% Et | Sample text: Furnace units schedule, drawing M-XXX
TABLE C403.3.2(5) | Minimum efficiency requirements: gas- and oil-fired boilers | Sample text: Gas fired, hot-water boiler 500,000 Btu/h input, B-1 | Sample text: 80% Et | Sample text: 83% Et | Sample text: Boiler schedule, drawing M-XXX
TABLE C403.3.2(6) | Water chilling packages - efficiency requirements | Sample text: new air cooled chiller, 200 ton | Sample text: PATH A: >10.1 EER @ Full load, 14.0 IPLV OR PATH B: >9.7 EER @ Full load, 16.1 IPLV | Sample text: 10.2 EER @ Full load, 15 IPLV | Sample text: Chiller schedule, drawing M-XXX
TABLE C403.3.2(7) | Minimum efficiency requirements: heat rejection equipment | Sample text: new axial fan open circuit cooling tower, 200 tons | Sample text: 40.2 gpm/hp | Sample text: 40.2 gpm/hp | Sample text: Chiller schedule, drawing M-XXX
TABLE C403.3.2(9) | Heat Transfer Equipment | Sample text: Liquid-to-liquid heat exchanger | Sample text: minimum efficiency not required, tested to AHRI 400 | Sample text: minimum efficiency not required, tested to AHRI 400 | Samples text: Equipment schedule, drawing M-XXX
TABLE C403.3.2(10) | Minimum efficiency requirements: electrically operated variable-refrigerant-flow air conditioners | Sample text: VRF air cooled air conditioner, 72,000 Btu/h (condenser capacity) | Sample text: 11.2 SEER, 15.5 IEER | Sample text: 11.5 SEER, 18.1 IEER | Samples text: VRF equipment schedule, drawing M-XXX
TABLE C403.3.2(11) | Minimum efficiency requirements: electrically operated variable-refrigerant-flow air-to-air and applied heat pumps | Sample text: VRF heat pump, without heat recovery, 72,000 Btu/h (condenser capacity) | Sample text: 11.0 EER, 14.6 IEER (cooling) 3.3 COPH (heating) | Sample text: 11.5 EER, 18.1 IEER (cooling) 3.5 COPH (heating) | Samples text: VRF equipment schedule, drawing M-XXX
C403.3.3 | Hot Gas Bypass Limitation | Sample text: 75kbtu/h unitary package | Hot gas bypass is allowed only on systems with multiple steps of unloading or continuous capacity modulation. Allowed Bypass capacity per Table C403.3.3 | Sample text: All cooling systems do not use hot gas bypass | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
C403.3.4, TABLE C403.3.4 | Boiler turndown | Sample text: Boilers B-1, B-2 turndown controls | Boiler systems with design input greater than 1,000,000 Btu/h shall comply with the turndown ratio specified in Table C403.3.4. | Sample text: Boiler B-1, B2 each have 7 to 1 turndown ratio | Sample text: See mechanical plans, M-1XX, M-1XX, M-1XX, mechanical control sequences, drawing M-XXX, and mechanical details M-XXX
C403.3.5 | Buildings with high efficiency space heating gas boiler systems | Sample text: Condensing boilers, gas-fired (B-1, B-2) | gas-fired condensing boilers with rated efficiency >90% Et shall be designed to operate in condensing mode. RWT < 120F. | Sample text: Return Water Temp (RWT) = 115F for B-1 and B-2 | Sample text: See mechanical plans, M-1XX, M-1XX, M-1XX, mechanical control sequences, drawing M-XXX, and mechanical details M-XXX
C403.4.1 | Thermostatic controls (Mandatory) | Sample text: Thermostats/humidistats for mechanical zones | Minimum one thermostat/humidistat required per zone | Sample text: One thermostat is provided for each zone | Sample text: Thermostats shown on mechanical plans, M-XX1, M-XX2, M-XX3.
C403.4.1.1 | Heat pump supplementary heat (Mandatory) | Sample text: 3 ton packaged heat pump with electrical heat, HP-1 | Except during defrost, supplementary electric heat to be prevented from coming on when heat pump can meet load | Sample text: Electric heat shall be enable only when the heat pump cannot meet load. | Sample text: See mechanical control sequences, drawing M-XXX.
C403.4.1.3 | Set point overlap restriction (Mandatory) | Sample text: Heat pump, split unit thermostats | Zone thermostat operation shall have minimum 5 °F dead band between heating and cooling | Sample text: Each thermostat will be programmed as required | Sample text: See mechanical control sequences, drawing M-XXX.
C403.4.1.4 | Heated or cooled vestibules (mandatory) | Sample text: Entrance vestibule heating/cooling | heated vestibules to shut off when outdoor air temperature > 45F Heating setpoint <60F Cooling setpoint >85F | Sample text: Programmable thermostat in vestibule limits temperature to the code required setpoints. | Sample text: Thermostats shown on mechanical plans, M-XX1, M-XX2, M-XX3. See mechanical control sequences, drawing M-XXX.
C403.4.1.5 | Hot water boiler outdoor temperature setback control (Mandatory) | Sample text:B-1, boiler outdoor temperature setback controls | Hot water boilers that supply heat to the building through one- or two-pipe heating systems shall have an outdoor setback control that lowers the boiler water temperature based on the outdoor temperature | Sample text: HW boiler controls provided as per requirements | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
C403.4.2 | Off-hour controls (Mandatory) | Sample text: All zones | All zone thermostat shall be operated via thermostatic setback controls operated via an automatic time clock or a programmable control system | Sample text: Each thermostat will be programmable to meet requirements | Sample text: See mechanical control sequences, drawing M-XXX.
C403.4.2.1 | Thermostatic setback (Mandatory) | Sample text: All zones | Controls shall have ability to setback temperatures down to 55 °F (13°C) , or up to 85 °F | Sample text: Each thermostat will be programmable to meet requirements | Sample text: See mechanical control sequences, drawing M-XXX.
C403.4.2.2 | Automatic setback and shutdown (Mandatory) | Sample text: All zones | Controls shall be capable of automatically starting and stopping the systems for seven different daily schedules per week, capable of having settings saved in memory for 10 hours during a loss of power, and a manual system "on" override for up to two hours, or an occupancy sensor | Sample text: Each thermostat will be programmable to meet requirements | Sample text: See mechanical control sequences, drawing M-XXX.
C403.4.2.2 | Automatic start (Mandatory) | Sample text: All zones | Controls shall be provided for each HVAC system and automatically adjusting the daily start time of the HVAC in order to bring each space to the desired temperature. | Sample text: Each thermostat will be programmable to meet requirements | Sample text: See mechanical control sequences, drawing M-XXX.
C403.4.3 | Hydronic Systems Controls | Sample text: Boilers B-1, B-2 | Heating systems consisting of multiple packaged boilers delivering conditioned water or steam into a common distribution system shall have automatic controls capable of sequencing boilers. Systems comprised of a single boiler and greater than 500,000 Btu/h input design capacity shall include either a multistaged or modulating burner. | Sample text: Multistaged boilers provided as per requirements | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
C403.4.3.1 | Three-pipe System | Sample text: Three Pipe Systems | Hydronic systems using a common return for both hot water and chilled water are prohibited | Sample text: Not applicable | Sample text: These systems are not used
C403.4.3.2 | Two-pipe Changeover System | Sample text: Two Pipe Changeover | Dead band for change-over is a minimum of 15 degrees F based on O.A., minimum operation in one mode for 4 hours before changeover, heating and cooling supply temperature no more than 30 degrees F apart at change-over point. | Sample text: Dead band controls as per requirements | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
C403.4.3.3 | Hydronic (Water Loop) Heat Pump Systems | Sample text: Water loop heat pump system controls | Hydronic heat pump systems shall comply with Sections C403.4.3.3.1 through C403.4.3.3.3. Minimum 20 degree F dead band between initiation of heat injection or heat rejection to water loop | Sample text: Heat pump system controls as per requirements | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
C403.4.3.3.1 | Temperature dead band | Sample text: Temperature dead band | Minimum 20 F dead band between initiation of heat injection or heat rejection to water loop | Sample text: 20 F deadband specified Dead band controls as per requirements | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
C403.4.3.3.2 | Heat Rejection | Sample text: CT-1, CT-2 | Heat rejection equipment shall comply with Sections C403.4.2.3.2.1 and C403.4.2.3.2.2. | Sample text: Open-circuit tower is used directly in the heat pump loop and an automatic valve shall be installed to bypass all heat pump water flow around the tower. | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
C403.4.3.3.3 | Two-position valve | Sample text: Two-position valve for WSHP 1,2 | Each hydronic heat pump on the hydronic system having a total pump system power exceeding 10 hp shall have a two-position valve. | Sample text: WSHP 1,2 controls provided as per requirements | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
C403.4.4 | Part-load controls: temperature reset controls | Sample text: Boilers B-1, B-2 reset controls | Hydronic systems greater than or equal to 300,000 Btu/h in design output capacity supplying heated or chilled water to comfort conditioning systems shall include controls that have the capability to do all of the items 1 to 3 listed in this section. | Sample text: Boiler controls provided as per requirements | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
C403.4.4 | Part-load controls: Pumps | Sample text: Hydronic pump controls | Hydronic system pumping power greater than or equal to 2 hp have variable flow systems and meet the requirements of this section | Sample text: Hydronic controls provided on hot water system as per requirements | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
C403.4.5 | Pump isolation | Sample text: Pumps CW-1 , HW-1 | Chilled water plants including more than one chiller shall have the capability to reduce flow automatically through the chiller plant when a chiller is shut down. Chillers piped in series for the purpose of increased temperature differential shall be considered as one chiller. Boiler plants including more than one boiler shall have the capability to reduce flow automatically through the boiler plant when a boiler is shut down. | Sample text: Pumps CW-1, HW-1 equipped with VFD controls as per requirements | Sample text: See mechanical plans, M-1XX, M-1XX, M-1XX, mechanical control sequences, drawing M-XXX, and mechanical details M-XXX
C403.5 | Economizers (Prescriptive) | Sample text: Economizers on RTU-1, RTU-2 | Air Economizer required for all cooling systems, unless an exception is met | Sample text: Economizer not required PTAC-1 through PTAC-5, Item 3 Individual cooling unit < 270,000 BTU/h Total cooling capacity for systems serving guest rooms- 1,222,000 BTU/h Economizer not required VRF-1 through VRF-5, exception 5 Minimum eff. Table C403.3.2(11): 11.0 EER High eff. exemption limit: 13.2 EER Proposed VRF: 13.5 EER | Sample text: See mechanical schedule, M-4XX
C403.5.1 | Integrated economizer control | Sample text: Economizer control on RTU-1, RTU-2 | Economizer systems shall be integrated with the mechanical cooling system and be capable of providing partial cooling even where additional mechanical cooling is required to provide the remainder of the cooling load. Controls shall not be capable of creating a false load in the mechanical cooling systems by limiting or disabling the economizer or any other means, except at the lowest stage of mechanical cooling. | Sample text: Economizers systems are integrated with the mechanical cooling system and capable of providing partial cooling, per control sequence | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
C403.5.2 | Economizer heating system impact | Sample text: Economizer heating system impact | Economizer operation does not increase building heating energy use during normal operation | Sample text: Economizer operation does not increase building heating energy use during normal operation | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
C403.5.3 | Air economizers | Sample text: Air economizers, RTU-1 | Air economizers shall be configured to provide up to 100% of design supply air quantity as outdoor air for cooling. Economizer controls/dampers configured to sequence dampers with the cooling equipment. Fixed dry-bulb control, high limit shutoff when outdoor air Temp > 65. Systems capable of relieving excess outdoor air during economizer operation. | Sample text: Air economizer system controls, As per requirements | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
C403.5.4 | Water-side economizers | Sample text: Water-side economizer, WSHP-1 through WSHP-5 | Water economizers shall be configured to cool supply air and provide 100% of expected cooling load at outdoor air temp <50Fdb, <45Fwb. Water economizer system shall have water-side pressure drop of < 15 feet OR a secondary loop | Sample text: Water economizer systems controls provided as per requirements. | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
C403.5.5 | Economizer fault detection and diagnostics (Mandatory) | Sample text: RTU-1, Economizer fault detection and diagnostics | Air-cooled unitary direct-expansion units and VRF units which have an economizer must include a fault detection and diagnostics system which complies with items 1-7 listed in Section C403.5.5 | Sample text: RTU-1 includes economizer with fault detection and diagnostic controls, per requirements | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
C403.6.1 | Variable air volume and multiple-zone systems | Sample text: VAV system serving zones 1 through 4 | VAV system with multiple zone, primary air to each zone shall be reduced to a minimum requirements before reheating, recooling, or mixing takes place. | Sample text: control sequences provided as required | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
C403.6.2 | Single-duct VAV system, terminal devices | Sample text: single duct VAV system in zone XX | Terminal devices shall be capable of reducing primary supply air before reheating or recooling takes place | Sample text: control sequences provided as required | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
C403.6.3 | Dual-duct and mixing VAV systems, terminal devices | Sample text: dual duct mixing VAV system in zone XX | Terminal devices shall be capable of reducing air from one duct to a minimum before mixing takes place | Sample text: control sequences provided as required | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
C403.6.4 | Single-fan dual-duct and mixing VAV systems, economizers | Sample text: dual duct mixing VAV system in zone XX | Individual dual duct or mixing heating and cooling systems with a single fan and capacities greater than 90,000 Btu/h shall not be equipped with air economizers | Sample text: economizer not provided as per requirements | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
C403.6.5 | Supply-air temperature reset controls | Sample text: HVAC system serving zones 5-XX | Control system shall automatically reset supply-air temperature in response to building load or outdoor air temperature. The controls shall be capable of resetting the supply air temperature not less than 25% of the difference between the design supply-air temperature and the design room air temperature. | Sample text: control sequences provided as required | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
C403.6.6 | Multiple zone VAV system ventilation optimization control | Sample text: Multi zone systems with DDC of zone boxes | Control system shall have automatic controls configured to reduce OA intake flow below design rates in response to changes in system ventilation efficiency | Sample text: control sequences provided as required | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
C403.6.7 | Parallel-flow fan-powered VAV air terminal control | Sample text: Parallel-flow fan-powered VAV controls | Parallel-flow fan-powered VAV controls have automatic controls configured to: 1. terminal fan is off when space heating is required or where required for ventilation 2. Turn on terminal fan as first stage of heating before heating coil is activated 3. During heating for warmup or setback temperature control, operate terminal fan and heating coil without primary air | Sample text: control sequences provided as required | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
C403.6.8 | Setpoints for direct digital control | Sample text: VAV box Control set points | Systems with DDC (direct digital control) controlled VAV boxes shall reset based on zone requiring greatest pressure | Sample text: reset based on zone XXX | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
C403.6.9 | Static pressure sensor location | Sample text: VAV fans | Static pressure sensors used to control VAV fans shall be located such that the controller set point is not greater than 1.2 inches w.c.. Where this results in one or more sensors being located downstream of major duct splits, not less than one sensor shall be located on each major branch to ensure that static pressure can be maintained in each branch. | Sample text: Static sensor used to control VAV fans shall be as required | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
C403.7.1 | Demand control ventilation (Mandatory) | Sample text: RTU-1, DCV system in auditorium | Required in spaces greater than 500 square feet and occupant density of 25 people per 1000 square feet or greater | Sample text: RTU-1 includes a DCV system provided as per requirements | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
C403.7.2 | Enclosed parking garage ventilation controls (Mandatory) | Sample text: Enclosed parking garage ventilation control requirements | Shall have contamination-sensing devices and automatic controls configured to stage fans or modulate fan average airflow rates to 50% or less of design capacity, or intermittently operate fans less than 20% of the occupied time or as required to maintain acceptable contaminant levels in accordance with NYC MC | Sample text: Enclosed parking garage fan equipped with VFD controls as per requirements | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
C403.7.3 | Ventilation air heating control ( Mandatory) | Sample text: RTU-1 | Units that provide ventilation air and operate in conjunction with heating/cooling systems shall not warm supply air to greater than 60F when majority of zones require cooling. | Sample text: control sequences provided as required | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
C403.7.4, TABLES C403.7.4(1) & C403.7.4(2) | Energy recovery ventilation systems (Mandatory) | Sample text: MAU-1, energy recovery wheel | Required in systems with design air capacity and (%) outdoor air at full design flow rate shown in Tables C403.7.4(1) and C403.7.4(2). Minimum 50% total effectiveness. | Sample text: Energy recovery wheel provided with 65% efficacy and economizer bypass | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
C403.7.5 | Kitchen exhaust systems (Mandatory) | Sample text: Kitchen exhaust systems | Replacement air introduced directly into the hood cavity of kitchen exhaust hoods shall not exceed 10% of the hood exhaust airflow rate. Conditioned supply air delivered to any space shall not exceed the greater of the items listed in this section of this code | Sample text: Kitchen exhaust system provided as per requirements | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
C403.7.6 | Automatic control of HVAC systems serving guestrooms (Mandatory) | Sample text: HVAC control in All hotel rooms | In hotels and motels with greater than 50 guest rooms, automatic control for the HVAC equipment and ventilation system serving each guest room shall be configured to setback or turn off when unoccupied. | Sample text: Guest rooms provided with Captive key card system as per requirements. | Sample text: See mechanical details, drawing M-XXX, mechanical plans, M-1XX, M-1XX, M-1XX, mechanical control sequences, drawing M-XXX
C403.7.7 | Shutoff dampers (Mandatory) | Sample text: Outdoor air intake, exhaust openings, stairway and shaft vents | Each outdoor supply air and exhaust air ducts shall be provided with motorized dampers to shut off or open as required by this section. Class I motorized damper with a maximum air leakage rate of 4cfm/ft2 of damper surface area at 1.0 inch water gauge. | Sample text: Class I motorized damper with a maximum air leakage rate of 4cfm/ft2 of damper surface area at 1.0 inch water gauge | Sample text: See mechanical plans, M-XX1, M-XX2, M-XX3, mechanical control sequences, drawing M-4XX
C403.8.1, TABLES C403.8.1(1) & C403.8.1(2) | Allowable Fan Horsepower (Mandatory) | Sample text: Exhaust Fans, TX-1 through TX-5, KX-1 through KX-5 | Total system fan hp shall not exceed limits in Table C403.8.1(1) | Sample text: Total Fan power = XXX bhp | Sample text: See mechanical details, drawing M-XXX
C403.8.2 | Motor nameplate horsepower (Mandatory) | Sample text: Exhaust Fans, TX-1 through TX-5, KX-1 through KX-5 | Motor selection does not except 1.5xbhp for fans less than 6bhp | Sample Text: Fan hp < 8 hp hp = 1.5 * 5.5bhp | Sample text: See mechanical details, drawing M-XXX
C403.8.3 | Fan Efficiency (Mandatory) | Sample text: Fan efficiency for AHU-1, 2, 3 | Minimum FEG = 67 | Sample text: Minimum FEG = 70 | Sample text: See mechanical details, drawing M-XXX
C403.8.4 | Fractional hp fan motors (Mandatory) | Sample text: Fractional hp fan motors | Motor fans 1/12 hp to 1 hp shall be electronically commutated motors or have a minimum efficiency of 70% and must have the means to adjust motor speed for either balancing or remote control. The use of belt-driven fans to sheave adjustments for airflow balancing instead of varying motor speed are permitted. | Sample text: Motor fan 1 hp and efficiency 70% | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
C403.8.5.1 | Fan Airflow control | Sample text: Fan controls for single-zone DX cooling system 135kBTU/h | Supply fans controlled by variable speed drives and configured to requirements in C403.8.5.1. | Sample text: Variable speed fan controls provided per requirements | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
C403.9 | Heat rejection equipment | Sample text: Cooling Towers, CT-1, CT-2 | Fans shall be able to operate at 2/3 speed or less, and have controls to adjust fan speed based on demand | Sample text: Fans on CT-1, CT-2 equipped with VFD controls per requirements | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
C403.9.5 | Heat Recovery for Service Water Heating | Sample text: Water cooled Chiller plant = 2 million BTU/h | Provide condenser water heat recovery, required for 24 hr/day operations, with water cooled systems over 6 million btu/h | Sample text: not applicable | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
C403.10 | Refrigeration equipment performance | Sample text: Minimum efficiency requirements for commercial refrigeration and commercial refrigerators and freezers | Refrigeration equipment shall have an energy use in kWh/day not greater than the values of Tables C403.10.1(1) and C403.10.1(2) | Sample text: Commercial refrigerators provided as per requirements | Sample text: See mechanical details, drawing M-XXX, mechanical plans, M-1XX, M-1XX, M-1XX, mechanical control sequences, drawing M-XXX
C403.10.4 | Refrigeration systems | Sample text: Refrigeration systems | Refrigerated display cases, walk-in coolers or walk-in freezers that are served by remote compressors and remote condensers not located in a condensing unit, shall comply with Sections C403.10.4.1 and C403.10.4.2. | Sample text: Refrigeration systems provided as required | Sample text: See mechanical schedule, M-4XX, mechanical control sequences, drawing M-XXX
C403.11.1 | Duct and plenum insulation and sealing (Mandatory) | Sample text: All ductwork | Supply and return ducts and plenums in shall have a minimum of R-6 where located in unconditioned spaces and R-8 minimum where located outside the building. Where located within a building envelope assembly, the duct or plenum shall be separated from the building exterior or unconditioned or exempt spaces by a minimum of R-8. | Sample text: Unconditioned spaces: R-6 Conditioned spaces: None, exterior wall insulated >R-8 | Sample text: See mechanical drawing M-XXX
C403.11.2 | Duct Construction (Mandatory) | Sample text: Ductwork | Shall be constructed and erected in accordance with the NYCMC | Sample text: Ductwork must be constructed and erected in accordance with the NYCMC | Sample text: See mechanical drawing M-XXX
C403.11.2.1 | Low-Pressure Duct Systems (Mandatory) | Sample text: Low Pressure Ductwork | All low pressure ducts, operating at 2" of W.G. or less shall be properly sealed with approved methods | Sample text: All low pressure ducts properly sealed as per requirements | Sample text: See mechanical drawing M-XXX
C403.11.2.2 | Medium-Pressure Duct Systems (Mandatory) | Sample text: Medium Pressure Ductwork | Ducts operating between 2" and 3" W.G. shall be insulated and sealed per C403.11.1 and must be clearly indicated on the construction documents in accordance with NYCMC | Sample text: all medium pressure ducts sealed as per requirements and insulated to R-XX | Sample text: See mechanical drawing M-XXX
C403.11.2.3 | High Pressure Duct Systems (Mandatory) | Sample text: High Pressure Ductwork | Ducts operating in excess of 3" W.G. shall be insulated and sealed per C403.11.1 and leak tested per code requirements with a rate of air leakage (CL) less than or equal to 4.0 | Sample text: all high pressure ducts sealed as per requirements and insulated to R-8. All ducts leak tested to < 4.0, per Equation 4-8 | Sample text: See mechanical drawing M-XXX
TABLE C403.11.3 | Minimum Piping Insulation Thickness | Sample text: Boiler piping insulation, mini-split refrigerant insulation | Sample text: Boiler piping insulation: 105-140F, 1-1.5" diameter = 1.0 inches Refrigerant insulation: <40F, < 1" diameter = 0.5 inches | Sample text: Boiler piping insulation: 1.5 inches Refrigerant insulation: 0.5 inches | Sample text: See mechanical drawing M-XXX
C403.11.3.1 | Protection of piping insulation (Mandatory) | Sample text: Piping located outdoors | All piping insulation is protected from damage, including that due to sunlight, moisture, equipment maintenance and wind. Adhesive tape is not permitted. | Sample text: All outdoor piping insulation is protected from damage by using (XXXX - type of material). | Sample text: See mechanical drawing M-XXX
C403.12.1 | Heating Outside a Building | Sample text: Parking Garage heating | All heating systems installed outdoors shall be of the radiant type, with an occupancy switch or timer switch. | Sample text: Radiant heat system provided as per requirements | Sample text: See mechanical details, drawing M-XXX, mechanical plans, M-1XX, M-1XX, M-1XX, mechanical control sequences, drawing M-XXX
C403.12.2 | Snow- and ice-melt system controls | Sample text: Snow- and ice-melt system at carport | Automatic controls shall shutoff snowmelt systems when pavement temperature is above 50°F and no precipitation is falling and automatic or manual control to shutoff the system when the outdoor temperature is above 40°F | Sample text: Snow-and ice-melt system programmable to meet requirements | Sample text: See mechanical plans, M-XX1, M-XX2, M-XX3, mechanical control sequences, drawing M-4XX
C403.12.2 | Freeze protection system controls | Sample text: Heat tracing of outdoor piping | Freeze protection systems shall include automatic controls shall shut off the systems when outdoor air temperatures are above 40°F or when the conditions of the protected fluid will prevent freezing | Sample text: Heat tracing of outdoor piping shall include automatic controls that shut off the systems when outdoor temperatures are above 40°F or when the conditions of the protected fluid will prevent freezing | Sample text: See mechanical plans, M-XX1, M-XX2, M-XX3, mechanical control sequences, drawing M-4XX
C408.2 | Mechanical, renewable energy, and service water heating systems commissioning and completion requirements | Sample text: Commissioning | Mechanical systems shall be commissioned and completed in accordance with Section C408 | Sample text: Total building heating capacity = 750,000 BTU/h Total cooling capacity = 620,000 BTU/h Commissioning is required for this project per requirements | Sample text: See mechanical drawing M-XXX

## Com.ECC - DHW
2020 NYCECC Tabular Analysis Commercial Building in compliance with ECC
Energy Code Scope of Work
For all ALTERATION job applications where the proposed scope of alteration work is limited to partial areas of the existing buildings and/or conditions, please provide a detailed description of the proposed scope of work here, and itemize the altered elements in the tabular format below.
Note for ALTERATION job application: For each altered element where ALTERATION-specific exception/allowance is applied, create a row in the table to cite the applicable code section and to report the Supporting Documentation location. For examples of ALTERATION-specific exceptions/allowances, refer to 101.2.5, C503.1, C503.6, and C504.2.
NYCECC Citation | Provision | Item Description | Code Prescriptive Value (ECC) | Proposed Design Value | Supporting Documentation
C404.2 Table C404.2 | Service water-heating Equipment Performance Efficiency | Sample text: Domestic Water Heater, DWH-1,-2 | Shall meet efficiency requirements of table C404.2. If capacity is 1 MBH or greater, 90% Et or greater is required in Section C404.2.1 | Sample text: 92% Et, Gas-fired, (2) 500,000 Btu/h | Sample text: See plumbing schedules, drawing P-XXX
C404.3 | Heat traps for hot water storage tanks | Sample text: Heat traps | Water-heating equipment shall be provided with heat traps on the supply and discharge piping if not integrated with the equipment. | Sample text: Brand XXX water heating equipment supplied with integral heating traps | Sample text: See plumbing schedules, drawing P-XXX
C404.4 | Insulation of piping | Sample text: DHW insulation | Sample text: DHW piping insulation: 105-140F, 1-1.5" diameter = 1.0 inches | Sample text: DHW insulation = 1.0 inches | Sample text: See plumbing schedules, drawing P-XXX
C404.5 | Efficient heated water supply piping | Sample text: DHW efficient heated water design | One of the following items is required: 1. Max. allowable pipe length - list nominal pipe size, maximum pipe length per table C404.5.1. 2. Max. allowable pipe volume method - list nominal pipe size, maximum volume per foot length, total maximum volume based on proposed design length, per Table C404.5.1. | Sample text: Compliance with max. allowable pipe length method. | Sample text: See plumbing specification drawings, P-XXX
C404.5.1 Table C404.5.1 | Maximum allowable pipe length method | Sample text: DHW 1/2" piping | Sample text: Maximum allowable piping length from nearest source of heated water to the termination of the fixture supply shall not exceed a maximum distance of 43 feet | Sample text: Maximum distance from DHW riser to residential lavatory is 30 ft | Sample text: See plumbing specification drawings, P-XXX
C404.5.2 Table C404.5.1 | Maximum allowable pipe volume method | Sample text: DHW 1/2" piping | Sample text: Maximum allowable piping volume from nearest source of heated water to the termination of the fixture supply shall not exceed 2 ounces for any public lavatory fixture or 0.5 gallons for any other fixture. | Sample text: Maximum volume of water from DHW riser to residential lavatory is 0.4 gallons | Sample text: See plumbing specification drawings, P-XXX
C404.6 | Heated-water circulating and temperature maintenance systems | Hot water circulation pumps and heat trace | The system return pipe shall be a dedicated return pipe or cold water supply pipe. Controls for circulating hot water system pumps shall start the pump based on the identification of a demand for hot water within the occupancy. The controls shall automatically turn off the pump when the water in the circulation loop is at the desired temperature and when there is no demand for hot water. Gravity and thermo-syphon circulation systems shall be prohibited. Heat trace shall be arranged to be turned off automatically when there is no hot water demand. | Sample text: DHW circulation pump controls provided as required | Sample text: See plumbing specification drawings, P-XXX
C404.7 | Demand recirculation controls | Demand recirculation controls | The control shall start the pump upon receiving a signal from the action of a user of a fixture or appliance, sensing the presence of a user of a fixture or sensing the flow of hot or tempered water to a fixture fitting or appliance. The control shall limit the temperature of the water entering the cold-water piping to 104 degrees F (40 degrees C). | Sample text: Demand recirculation controls provided per requirements | Sample text: See plumbing specification drawings, P-XXX
C404.8 | Drain water heat recovery units | Drain water heat recovery units | Potable waterside pressure loss shall be less than 10 psi at maximum design flow. For Group R occupancies, the efficiency of drain water heat recovery unit efficiency shall be in accordance with CSA B55.1. | Sample text: Drain water heat recovery not provided. | Sample text: See plumbing specification drawings, P-XXX
C404.9 | Energy consumption of pools and permanent spas (Mandatory) | Sample text: Pool and Permanent Spa Controls | Shall be controlled by the requirements in Sections C404.9.1 through C404.9.3. | Sample text: Pool heaters and pump motors provided with controls as per requirements. | Sample text: See plumbing specification drawings, P-XXX
C404.9.3 | Covers | Sample text: Pool Covers for outdoor heated pool | Outdoor heated pools and outdoor permanent spas shall be provided with a vapor-retardant cover or other approved vapor-retardant means. | Sample text: Outdoor heated pools equipped with a vapor-retardant cover | Sample text: See plumbing specification drawings, P-XXX
C404.10 | Energy consumption of portable spas (Mandatory) | Sample text: Energy consumption of portable spas | The energy consumption of electric-powered portable spas shall be controlled by the requirements of APSP 14. | Sample text: The energy consumption of electric-powered portable spas shall be controlled by the requirements of APSP 14. | Sample text: See plumbing specification drawings, P-XXX
C408.2 | Mechanical, renewable energy, and service water heating systems commissioning and completion requirements | Sample text: Service water-heating system commissioning and completion requirements | Service water-heating systems, swimming pool water-heating systems, spa water-heating systems and the controls for those systems shall be commissioned and completed in accordance with Section C408.2. | Sample text: Total heating capacity (including Service Water) = 750,000 BTU/h Commissioning will be performed per requirements. | Sample text: See plumbing specification drawings, P-XXX

## Com.ECC - Lighting
2020 NYCECC Tabular Analysis Commercial Building in compliance with ECC
Energy Code Scope of Work
For all ALTERATION job applications where the proposed scope of alteration work is limited to partial areas of the existing buildings and/or conditions, please provide a detailed description of the proposed scope of work here, and itemize the altered elements in the tabular format below.
Note for ALTERATION job application: For each altered element where ALTERATION-specific exception/allowance is applied, create a row in the table to cite the applicable code section and to report the Supporting Documentation location. For examples of ALTERATION-specific exceptions/allowances, refer to 101.2.5, C503.1, C503.6, and C504.2.
NYCECC Citation | Provision | Item Description | Code Prescriptive Value (ECC) | Proposed Design Value | Supporting Documentation
C405.1 | Dwelling Unit Lighting | Sample text: Dwelling unit lighting fixtures | Not less than 90% of the lamps in permanently installed lighting fixtures shall use lamps with an efficacy of at least 65 lumens per watt, or have a total luminaire efficacy of at least 45 lumens per watt. | Sample text: All lamps in fixtures are 68 lumens per watt. | Sample text: see drawing E-XXX (Lighting fixture schedules)
C405.2 | Lighting controls (Mandatory) | Sample text: interior lighting controls include occupancy sensors, daylight responsive controls, bi-level controls, and automatic shut-off | Lighting systems shall be provided with controls as specified in Sections C405.2.1 through C405.2.6. | Sample text: Occupancy sensors in restrooms, conference rooms, open offices; daylight responsive controls in all offices; bi-level controls in stairwells; automatic shut-off via BMS for all lighting | Sample text: see drawing EN-XXX (Lighting fixture schedule & narratives)
C405.2.1, C405.2.1.1, C405.2.1.2 | Occupant sensor controls | Sample text: Occupant sensor controls are provided in each conference room, restroom, storage area, corridor, stairwell and open plan office | Sample Text: Occupant sensors required in each restroom, storage area, corridor, stairwell and open plan office. Vacancy sensors (manual-on, auto-off) required in each conference room. | Sample text: Occupancy & vacancy sensors provided with 15 minute shut off limit. Manual-off vacancy sensors required in conference rooms. | Sample text: see drawing E-XXX (lighting fixture schedule & narratives)
C405.2.1.3 | Occupant sensor control function in open plan office areas, cafeteria dining areas, and fast food dining areas | Sample text: Occupant sensor control function in open plan offices | Sample text: Open plan office occupancy controls shall comply with all of the following: 1. general lighting controlled by control zones < 600 sq ft 2. lighting automatically turns off in all control zones within 15 min after all occupants left the open plan office 3. General lighting power in each control zone is reduced by not less than 80% of full zone lighting power in a uniform illumination pattern within 15 min of all occupants leaving the control zone. 4. Daylight responsive control will activate open plan offices lighting only when occupancy is detected. | Sample text: Open plan office occupancy controls are configured as per code requirements | Sample text: see drawing E-XXX (lighting fixture schedule & narratives)
C405.2.1.4 | Occupant sensor control function for egress illumination | Sample text: Occupant sensor controls for egress illumination | Sample text: All luminaires serving the exit access, corridors, stairwells shall contain occupancy sensors that reduce the lighting power by 50 percent when unoccupied for a period longer than 15 minutes. | Sample text: Exception 1 applies to all corridors and stairwells. The total lighting is less than 0.02 watts /sq ft. | Sample text: see drawing EN-XXX (Lighting fixture schedules)
C405.2.2, | Time-switch controls | Sample text: Time-switch controls at room XX-X | Each area of the building that is not provided with occupant sensor controls complying with Section C405.2.1.1 shall be provided with time switch controls complying with Section C405.2.2.1. Exception: Where a manual control provides light reduction in accordance with Section C405.2.2.2, automatic controls shall not be required for the following: 1. Sleeping units. 2. Spaces where patient care is directly provided. 3. Spaces where an automatic shutoff would endanger occupant safety or security. 4. Lighting intended for continuous operation. 5. Shop and laboratory classrooms. | Sample text: All areas of the building are provided with occupancy sensors - time-switch controls not required. | Sample text: see drawing E-XXX (Lighting fixture schedules & narratives)
C405.2.2.1 | Time-switch control function | Sample text: Time-switch controls | Each space provided with time-switch controls shall also be provided with a manual control for light reduction in accordance with section C405.2.2.2. Time-switch controls shall include an override switching device that complies with the following: 1. Have a minimum 7-day clock. 2. Be capable of being set for seven different day types per week. 3. Incorporate an automatic holiday "shutoff" feature, which turns off all controlled lighting loads for at least 24 hours and then resumes normally scheduled operations. 4. Have program backup capabilities, which prevent the loss of program and time settings for at least 10 hours, if power is interrupted. 5. Include an override switch that complies with the following: 5.1. The override switch shall be a manual control. 5.2. The override switch, when initiated, shall permit the controlled lighting to remain on for not more than 2 hours. 5.3. Any individual override switch shall control the lighting for an area not larger than 5,000 square feet (465m²). Exceptions as per this code section. | Sample text: Time-switch controls provided as required. | Sample text: see drawing E-XXX (Lighting fixture schedules & narratives)
C405.2.2.2 | Light-reduction controls | Sample text: Light-reduction controls | Spaces required to have light-reduction controls shall have a manual control that allows the occupant to reduce the connected lighting load in a reasonably uniform illumination pattern by at least 50 percent. | Sample text: Light-reduction controls provided in open space on 5th floor. | Sample text: see drawing E-XXX (Lighting fixture schedules & narratives)
C405.2.3 | Daylight-responsive controls | Sample text: Daylight-responsive controls. | Daylight responsive controls complying with Section C405.2.3.1 shall be provided to control the electric lights within daylight zones in the following spaces: 1. Spaces with a total of more than 100 watts of general lighting within sidelight daylight zones complying with Section C405.2.3.2. General lighting does not include lighting that is required to have specific application control in accordance with Section C405.2.4. 2. Spaces with a total of more than 100 watts of general lighting within toplight daylight zones complying with Section C405.2.3.3. | Sample text: N/A Daylight responsive controls are not required for the following: Dwelling units and sleeping units. (Exception #2) | See drawing EN-XXX
C405.2.3.1 | Daylight-responsive control function | Sample text: Daylight-responsive controls | Where required, daylight-responsive controls shall be provided within each space for control of lights in that space and shall comply with requirements of C405.2.3.1. | Sample text: Daylight-responsive controls shall be provided as per C405.2.3.1. | See drawing EN-XXX
C405.2.3.2 | Sidelight daylight zone | Sample text: Sidelight daylight zones, Floors 2-10 | The sidelight daylight zone is the floor area adjacent to vertical fenestration which complies with C405.2.3.2 | Sample text: Sidelight daylight zones provided as per C405.2.3.2.Sidelit zone area provided on drawings. | See drawing EN-XXX
C405.2.3.3 | Toplight daylight zone | Sample text: Toplight daylight zone, Floor 10 | The toplight daylight zone is the floor area underneath a roof fenestration assembly which complies withC405.2.3.3. | Sample text: Toplight daylight zone on 5th floor complies with C405.2.3.3.Toplit zone area provided on drawings. | See drawing EN-XXX
C405.2.4 | Specific application controls | Sample text: Retail display case lighting | Specific application controls shall be provided for the following: 1. Display and accent light shall be controlled by a dedicated control that is independent of the controls for other lighting within the room or space. 2. Sleeping units have controls to automatically switch off all luminaires and switched receptacles within 20 minutes 3. Permanently installed luminaires within dwelling units have time-switch or light reduction controls 4. Nonvisual applications shall be controlled by a time-switch that is independently controlled from the general lighting in the room or space | Sample text: Display and accent light D4 to D9 shall be controlled by a dedicated control that is independent of the controls for other lighting within the room or space. | Sample text: see drawing EN-XXX
C405.2.5 | Manual controls | Sample text: Manual controls | Sample text: Manual controls shall be in a location with ready access to occupants and located where the controlled lights or visible or shall identify the area served by the lights and indicate their status | Sample text: Manual controls are per code. | Sample text: see drawing E-XXX (lighting fixture schedule & narratives)
C405.2.6, C405.2.6.1, C405.2.6.2, C405.2.6.3, C405.2.6.4 | Exterior lighting controls | Sample text: Exterior lighting controls | Exterior lighting system shall be provided with controls that comply with the following: 1. Lights shall be automatically turned off when daylight is present and satisfies the lighting needs 2. Building façade lighting and landscape lighting shall shut off not later than 1 hour after business closing to not earlier than 1 hour before business opening OR shall be controlled so the total wattage is reduced by not less than 50% by shutting off the lighting or dimming luminaires 3. Time switch controls shall have a clock capable of programming for >7 days, and being set for 7 different day types per week, have an automatic holiday setback feature, and have backup capabilities | Sample text: Lighting on the north building facade equipped with photosensors. See lighting Plan. | See drawing EN-XXX
C405.2.6.1, C405.2.6.2, C405.2.6.4 | Exterior decorative lighting controls | Sample text: Exterior decorative lighting controls | Building façade lighting and landscape lighting shall shut off not later than 1 hour after business closing to not earlier than 1 hour before business opening OR shall be controlled so the total wattage is reduced by not less than 50% by shutting off the lighting or dimming luminaires | Sample text: Lighting on the south building facade equipped with dimmable controls set to 50% power. See lighting Plan. | Sample text: see drawing E-XXX (lighting fixture schedule & narratives)
C405.2.6.5 | Outdoor parking area lighting controls | Sample text: Outdoor parking lighting controls | Luminaires having rated input wattage > 78 W and a mounting height < 24 feet shall be controlled to automatically reduce the power by a minimum of 50% when no activity is detected for 15 min or less. No more than 1500 W of lighting power shall be controlled together. | Sample text: Outdoor parking area lighting poles are equipped with occupancy sensors, per requirements. | Sample text: see drawing E-XXX (lighting fixture schedule & narratives)
C405.3 | Interior lighting power requirements | Sample text: Interior lighting power requirements | Sample text: Open Office: 0.78 W/SF Conf Rm: 0.93 W/SF Stairwell: 0.50 W/SF Restroom: 0.75 W/SF The total connected interior lighting power shall be determined in accordance with Equation 4-10. | Sample text: Open Office: 0.68 W/SF Conf Rm: 0.92 W/SF Stairwell: 0.43 W/SF Restroom: 0.60 W/SF LPD value for building is less than the interior lighting power calculated under Section C405.3.2. See drawing EN-XXX. | Sample text: see drawing EN-XXX (Lighting fixture schedules)
C405.4 | Exterior lighting power requirements (Mandatory) | Sample text: Total connected load of proposed exterior lighting for lighting zone 3 | Sample text: 10.21 kW The exterior lighting power allowance shall be determined in accordance with Section C405.5.1. | Sample text: 7.66 kW The total exterior lighting power is less than the exterior lighting power calculated under Section C405.4. See drawing EN-XXX. | Sample text: A-XXX drawings (Reflected Ceiling Plans for all floors) E-XXX drawings (Reflected Ceiling Plans for all floors) E-XXX - XXX (Fixture schedule, control narrative, and details)
C405.5 | Electrical meter (Mandatory) | Sample text: Separate electrical meters have been provided for each dwelling unit. | Each dwelling unit located in a Group R-2 building shall have a separate electrical meter. | Sample text: meter at unit XXX through XXX | Sample text: See note in general notes (EN-XXX).
C405.6 | Electrical transformers (Mandatory) | Sample text: Electrical transformers | Electric transformers shall meet the minimum efficiency requirements of Table C405.6 | Sample text: Impedance transformers are exempted as per Exception # 8. | Sample text: See drawing EN-XXX for notes.
C405.7 | Electrical motors (Mandatory) | Sample text: Electrical motors | Electric motors shall meet the minimum efficiency requirements of Tables C405.7(l) through C405.7(4) when tested and rated in accordance with the DOE 10 CFR 431. The efficiency shall be verified through certification under an approved certification program or, where a certification program does not exist, the equipment efficiency ratings shall be supported by data furnished by the motor manufacturer. | Sample text: Electric motors are in compliance as per C405.7. See motor manufacturer data on drawing E-XXX. | Sample text: See drawing EN-XXX.
C405.8 | Vertical and horizontal transportation systems and equipment | Sample text: Elevators | New traction elevators with a rise of 75 feet or more shall have a power conversion system that complies with C405.8.1.1.1 through C405.8.1.1.3 | Sample text: Regenerative drives and occupancy sensors provided for elevators | Sample text: See drawing EN-XXX.
C405.10 | Commercial kitchen equipment | Sample text: Kitchen equipment in cafeteria | Sample text: Standard Open Deep-Fat gas Fryer: >50% heavy load cooking energy efficiency, <9,000 Btu/h Idle energy rate | Sample text: Standard Open Deep-Fat gas Fryer: >50% heavy load cooking energy efficiency, <9,000 Btu/h Idle energy rate | Sample text: See drawing EN-XXX.
C405.11 | Whole building energy monitoring | Whole building fuel metering | Sample text: Measurement devices shall be installed to individually monitor the energy use in each of the following types of energy supplied by a utility, energy provider, or plant that is not with the building: 1. natural gas 2. fuel oil 3. propane 4. steam 5. chilled water 6. hot water | Sample text: Whole building meters provided for Natural gas. See mechanical plans/electrical plans. | Sample text: See drawing EN-XXX.
C405.12 | Whole building electrical monitoring | Whole building electrical metering | Sample text: Measurement devices shall be installed to record electrical energy us every 60 minutes. | Sample text: Whole building meter provided for electricity. See mechanical plans/electrical plans. | Sample text: See drawing EN-XXX.

## Com.ECC - Add'l Eff
2020 NYCECC Tabular Analysis Commercial Building in compliance with ECC
Energy Code Scope of Work
For all ALTERATION job applications where the proposed scope of alteration work is limited to partial areas of the existing buildings and/or conditions, please provide a detailed description of the proposed scope of work here, and itemize the altered elements in the tabular format below.
Note for ALTERATION job application: For each altered element where ALTERATION-specific exception/allowance is applied, create a row in the table to cite the applicable code section and to report the Supporting Documentation location. For examples of ALTERATION-specific exceptions/allowances, refer to 101.2.5, C503.1, C503.6, and C504.2.
NYCECC Citation | Provision | Item Description | Code Prescriptive Value (ECC) | Proposed Design Value | Supporting Documentation
C406.1 | Requirements (for ADDITIONAL EFFICIENCY PACKAGE OPTIONS) | Sample text: Choose one of six additional efficiency options | Buildings shall comply with at least one of the following: 1. More efficient HVAC performance in accordance with Section C406.2. 2. Reduced lighting power density system in accordance with Section C406.3. 3. Enhanced digital lighting controls in accordance with Section C406.4. 4. Provision of a dedicated outdoor air system with energy recovery ventilation for certain HVAC equipment in accordance with Section C406.5. 5. High-efficiency service water heating in accordance with Section C406.6. 6. Enhanced envelope performance in accordance with Section C406.7 | Sample text: Reduced lighting power density system in accordance with Section C406.3. | Sample text: See note on EN-XXX
C406.2 | More efficient HVAC equipment performance | More efficient HVAC equipment performance | Sample text: Equipment exceeds code min. by 10%: 1 MBTU/hr gas-fired, hot water boiler @ 80% Et, 300 ton air-cooled chiller @ 10.1 EER, 14 IPLV | Sample text: 1000 MBH gas-fired, hot water boiler @ 96% Et, 300 ton air-cooled chiller @ 12 EER, 16 IPLV | Sample text: See Mechanical schedule, drawing M-XXX
C406.3 | Reduced lighting power density | Reduced lighting power density | Sample text: Lighting exceeds code min. by 10%: Building Area Method Office: 0.69 W/SF | Sample text: Building Area Method Office: 0.50 W/SF | Sample text: See RCPs, Lighting Schedule, LPD calculation, drawing A-XXX, EN-XXX
C406.4 | Enhanced digital lighting controls | Enhanced digital lighting controls | Interior lighting in the building shall have enhanced lighting controls that shall be located, scheduled and operated in accordance with Section C405.2.2 & C406.4 | Sample text: Office and lobby lighting provided as per requirements | Sample text: See RCPs, Lighting Schedule, LPD calculation, drawing A-XXX, EN-XXX
C406.5 | Dedicated outdoor air system | Dedicated outdoor air system with energy recovery | Buildings covered by Section C403.4 shall be equipped with an independent ventilation system designed to provide not less than the minimum 1OO percent outdoor air to each individual occupied space, as specified by the New York City Mechanical Code, and be equipped with an energy recovery system. | Sample text: MAU-1 provides 100% outside air provided to all occupied space and is equipped with an Energy Recovery device | Sample text: See Mechanical schedule, drawing M-XXX
C406.6 | Reduced energy use in service water heating | Reduced energy use in service water heating | At least 60% of the domestic hot water is provided by waste-heat recovery. Buildings shall be of the following types to use this compliance method: 1. Group R-I: Boarding houses, hotels or motels. 2. Group 1-2: Hospitals, psychiatric hospitals and nursing homes. 3. Group A-2: Restaurants and banquet halls or buildings containing food preparation areas. 4. Group F: Laundries. 5. Group R-2: Buildings with residential occupancies. 6. Group A-3: Health clubs and spas. | Sample text: 75% of DHW load provided by waste-heat from Cogeneration system *As a motel, Group R-1 building, this project complies to use this method. | Sample text: See Mechanical schedule, drawing M-XXX, EN-XXX
C406.7 | Enhanced envelope performance | Enhanced envelope performance | The thermal performance of the envelope shall demonatrate a minimum 15 % improvement compared to the requirements of Section C402.1.5. | Sample text: ComCheck displays 18% improvement beyond code minimum | Sample text: EN-100 sheet
C406.8 | Reduced air infiltration | Reduced air infiltration | Must show compliance through testing to no more than 0.25 cfm/ft2 of envelope area @ 75 PA and witnessed by the Progress Inspector as indicated on TR-8 inspection IIA7. | Building thermal envelope to be tested to no more than 0.4 cfm/ft2 of envelope area @ 75 PA and witnessed by the Progress Inspector as indicated on TR-8 inspection IIA7. | Sample text: EN-100 sheet
C408.2 | Mechanical renewable energy, and service water heating systems commissioning and completion requirements | Mechanical System Commissioning | Commissioning required on HVAC systems | Sample text: Commissioning will be performed on all HVAC systems Total building heating capacity: 1,585 MBH Total building cooling capacity: 1,400 MBH | Sample text: See total heating & cooling capacity calculation M-XXX, commissioning requirement note on EN-XXX