## Introduction
LOCAL LAW 87 - RETRO-COMMISSIONING DATA COLLECTION TOOL
Welcome to the Local Law 87 (LL87) Retro-Commissioning Data Collection Workbook from the New York City Department of Buildings. As part of the Greener, Greater Buildings Plan (GGBP), the City of New York enacted Local Law 87 which requires large buildings to undergo retro-commissioning once every ten years. This workbook captures critical information about your Lot/Building that should have been included in the retro-commissioning that was performed. New York City Department of Buildings will use the information found on this workbook to verify compliance with Local Law 87.
| For more information and to download a copy of Local Law 87/Rule visit: |  | https://www1.nyc.gov/site/buildings/business/energy-audits-and-retro-commissioning.page
| Questions or comments about this tool should be e-mailed to: | LL87@NYCsustainability.org
Tip #1: Only cells shaded in blue need to be entered/edited manually as mandatory fields. Enter "N/A" or leave as blank if a particular field does not apply. Do not "Change/Edit" white or grey cells.
Tip #2: Follow the formatting guidelines and/or instructions presented as pop-up comments (as indicated by a red triangle located in the upper right hand corner) for certain fields.
Tip #3: Provide a justification or explanation within the "Comments/Notes" window located at the bottom of each tab for any mandatory field entered as "N/A" or left blank.
Tip #4: Team Info(1), Building Info(1) and RCMs(1) tabs/sheets can be copied multiple times in their entirety manually, if needed for multiple buildings information entry. Do not Cut, Copy, Paste or Edit portions of sections within any sheet.
Tip #5: Use Energy Star Portfolio Manager Technical Reference "Thermal Energy Conversions" for all unit conversions/heat contents of each fuel type.
Note: This Retro-Commissioning tool is only a summary of a full Retro-Cx report. It does not replace the Retro-Commissioning report. A complete copy of the Retro-Commissioning report must also be submitted to the department for review and enforcement purposes. See AC §28-308.3.1 for the contents of the Retro-Commissioning report.

## Submittal Information
SUBMITTAL INFORMATION
Energy Efficiency Report (EER) Submission Information
| Submitted by: | Doe John
| Company: | 123 abc Development Inc.
| Phone: | (123) 456-7890
| Extension (If Applicable) | 1234
| E-mail: | JD@123abcDev.com
| Date: | 12/20/2020
| Filing Status: | Initial Filing
Lot Information
| Borough: | Manhattan
| Block: | 23450
| Lot: | 7890
| # of Buildings on Lot: | 1
Building(s) Information
| BIN | Address(es) | Zip Code
1 | 0101010 | 123 Sustainability Way | 00001
2 | 0101011 | 456 Green Zone Street | 00001
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
Comments/Notes: (If Applicable)
The above two listed BINs/buildings are on the same lot together exceeding 100,000 gsf and sharing a common central heating system as a shared "Based Building System".
Note on B8: Department of Buildings: Enter name of the professional/owner submitting this tool in the following format: last name then first name, separated by a space, not a comma.
Note on B10: Department of Buildings: Enter as (Area Code) xxx-xxxx
Note on B13: Department of Buildings: Date of submission of this Retro-Cx workbook to DOB. Format: MM/DD/YYYY
Note on B18: Department of Buildings: Enter tax block as assigned by Department of Finance. Must be entered as 5-digits without any commas, dashes or spaces. For example, enter 00001 for Block 1.
Note on B19: Department of Buildings: Enter tax lot as assigned by Department of Finance. Must be entered as 4-digits without any commas, dashes or spaces. For example, enter 0010 for Lot 10.
Note on B20: Department of Buildings: For each building enter BIN, Address and Zip Code in Building(s) Information section below.
Note on B23: Department of Buildings: Building Identification Number - Unique 7-digit Building Identification Number, assigned by City Planning, to a specific building. Enter all digits without any commas, dashes or spaces.

## Team Info
The Information in this tab is applicable to the following buildings:
TEAM INFORMATION
Retro-Commissioning Team Information |  | BIN(s)
0101010
Name of professional signing off: | Smith joe | 0101011
License: | PE
License #: | 012345
Organization/Company: | XYZ green consultants
Address: | 123 Green CT, New York, NY 00001
Telephone: | (212) 000-0001
Qualified Commissioning Agent: | Smith Joe
Years of Experience: | 10
Type of Certification: | Commissioning Process Professional certified by NEBB
Certification Expiration Date: | 12/20/2021
Retro-Commissioning Report Date: | 12/01/2020
Comments/Notes: (If Applicable)
Note on B9: Department of Buildings: last name first then first name, separated by a space, not a comma
Note on B15: Department of Buildings: Enter as (Area Code) xxx-xxxx
Note on B17: Department of Buildings: last name first then first name, separated by a space, not a comma
Note on B18: Department of Buildings: Enter years of experience performing Retro-Commissioning on buildings larger than 50,000 gross square feet. Enter in digit format e.g. enter as 1 not "one".
Note on B20: Department of Buildings: Format: MM/DD/YYYY
Note on B21: Department of Buildings: Enter date when final Retro-Commissioning report was submitted to the owner. Format: MM/DD/YYYY

## Building Info
The Information in this tab is applicable to the following buildings:
BUILDING INFORMATION
Building Contacts |  | BIN(s)
0101010
Building Owner: | 123 abc Development Inc. | 0101011
Owner's Representative: | None
Management Company: | Roe Jane Inc.
Property Management Contact Person: | Roe Jane
Telephone: | (212) 000-0002
Building Operator: | Doe Jane
Operator's Certification: | BOC
if "Other", please specify:
License # (if applicable): | Not Applicable
State: | New York
Comments/Notes: (If Applicable)
Note on B12: Department of Buildings: last name first then first name, separated by a space, not a comma
Note on B13: Department of Buildings: Enter as (Area Code) xxx-xxxx
Note on B15: Department of Buildings: last name first then first name, separated by a space, not a comma

## Inventory
MAJOR EQUIPMENT INVENTORY
Major Equipment Inventory (Group R Occupancies) | Boilers with rated input capacity ≥ 300,000 Btu/h | Chillers | Cooling towers and Dry coolers | Air Handling Units (AHU) ≥ 2,500 CFMs | Fan Coil Units (FCU) ≥ 2,500 CFMs | Heat Recovery Units (HRU) ≥ 2,500 CFMs | Heating and Ventilation Units (H&V) ≥ 2,500 CFMs | Packaged Air Conditioning Units ≥ 2,500 CFMs | Split Air Conditioning Units ≥ 2,500 CFMs | HVAC motors, fans and pumps ≥ 2.5 hp | Heat exchangers serving areas ≥ 10,000 sq.ft. | Domestic hot water heaters (storage and instantaneous) with rated input capacity > 155,000 Btu/h | Domestic water pumps ≥ 10 hp | The Information in this tab is applicable to the following buildings:
Quantity located in common areas | 2 | 2 | N/A | 2 | N/A | N/A | N/A | 1 | N/A | 3 | 1 | N/A | N/A | BIN(s)
Quantity located in non-common owner areas | 0 | 0 | N/A | 0 | N/A | N/A | N/A | 0 | N/A | 0 | 0 | N/A | N/A | 0101010
Quantity located in non-common tenant areas | 0 | 0 | N/A | 0 | N/A | N/A | N/A | 0 | N/A | 0 | 0 | N/A | N/A | 0101011
Sample (%) Tested (Common Areas) | 100% | 100% | N/A | 100% | N/A | N/A | N/A | 100% | N/A | 100% | 100% | N/A | N/A
Sample (%) Tested (Non-Common Owner Areas) | 0% | 0% | N/A | 0% | N/A | N/A | N/A | 0% | N/A | 0% | 0% | N/A | N/A
Sample (%) Tested (Non-Common Tenant Areas) | 0% | 0% | N/A | 0% | N/A | N/A | N/A | 0% | N/A | 0% | 0% | N/A | N/A
Date(s) Pre-testing verification conducted 1RCNY f(1)(i) | 10/1/2019; 11/7/2019 | 2019-06-07 | N/A | 9/7/2019; 10/1/2019 | N/A | N/A | N/A | 2019-07-20 | N/A | 10/1/2019; 12/10/2019 | 10/1/2019; 11/7/2019 | N/A | N/A
Date(s) Functional Performance Test (FPT) conducted 1RCNY f(1)(ii) | 11/7/2019; 11/20/2019; 12/10/2019 | 6/7/2019; 7/6/2019 | N/A | 9/7/2019; 10/1/2019 | N/A | N/A | N/A | 2019-07-20 | N/A | 2019-12-10 | 11/7/2019; 11/20/2019; 12/10/2019 | N/A | N/A
FPT forms provided in the Retro-Cx report | Yes | Yes | No | Yes | No | No | No | Yes | No | Yes | Yes | No | No
Major Equipment Inventory (Other than Group R Occupancies) | Boilers with rated input capacity ≥ 300,000 Btu/h | Chillers | Cooling towers and Dry coolers | Air Handling Units (AHU) ≥ 5,000 CFMs | Fan Coil Units (FCU) ≥ 5,000 CFMs | Heat Recovery Units (HRU) ≥ 5,000 CFMs | Heating and Ventilation Units (H&V) ≥ 5,000 CFMs | Packaged air conditioning units ≥ 5,000 CFMs | Split air conditioning units ≥ 5,000 CFMs | HVAC motors, fans and pumps ≥ 5 hp | Heat exchangers serving areas ≥ 10,000 sq.ft. | Domestic hot water heaters (storage and instantaneous) with rated input capacity > 155,000 Btu/h | Domestic water pumps ≥ 10 hp
Quantity located in common areas | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Quantity located in non-common owner areas | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Quantity located in non-common tenant areas | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Sample (%) Tested (Common Areas) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Sample (%) Tested (Non-Common Owner Areas) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Sample (%) Tested (Non-Common Tenant Areas) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Date(s) Pre-testing verification conducted 1RCNY f(1)(i) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Date(s) Functional Performance Test (FPT) conducted 1RCNY f(1)(ii) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
FPT forms provided in the Retro-Cx report | No | No | No | No | No | No | No | No | No | No | No | No | No
Comments/Notes: (If Applicable)
100% Multifamily Buildings with no occupancies "other than Group R". Only the "Major Equipment Inventory (Group R occupancies)" section applies.
Note on B16: Department of Buildings: Use semi colon (;) to separate multiple dates.
Note on B17: Department of Buildings: Use semi colon (;) to separate multiple dates.
Note on B27: Department of Buildings: Use semi colon (;) to separate multiple dates.
Note on B28: Department of Buildings: Use semi colon (;) to separate multiple dates.

## Identification
RETRO-COMMISSIONING TESTING SUMMARY
The Information in this tab is applicable to the following buildings:
| Deficiency Identified | Summary of Testing Methodology | BIN(s)
1RCNY 103-07 f(1) HVAC and Service Water Equipment |  |  | 0101010
Pre-testing verification | YES | RCM#9 RCM#10 RCM#11 Pre-testing verification checks for cleanliness and proper operation, primarily through visual observations, are conducted on the major equipment, associated sub-equipment and components. Pre-testing verifications checklists for Boilers (B-1 & B-2), Chillers (CH-1 and CH-2), AHUs (AHU-1 and AHU-2), Packaged AC unit (RTAC-1), Heat Exchanger (HX-1) and Pumps (P-1, P-2 and P-3), located in the common areas, can be found in the retro-commissioning report. | 0101011
Functional performance testing | YES | RCM#3 RCM#4 Functional performance testing has been conducted on all major equipment, associated sub-equipment and components located in the common areas. Functional performance test forms have been provided for Boilers (B-1 & B-2), Chillers (CH-1 and CH-2), AHUs (AHU-1 and AHU-2), Packaged AC unit (RTAC-1), Heat Exchanger (HX-1) and Pumps (P-1, P-2 and P-3) in the retro-commissioning report. Functional performance testing includes documentation on all functions related to controls sequence of operation, impacting energy consumption of the major equipment, economizer function, staging and load distribution, automatic reset functions and integrated system level testing. Testing results obtained though field observations, measurements, data logging and interviews with facility staff are documented within the forms.
Temperature and pressure setpoints and setbacks | YES | RCM#1 Temperature and pressure setpoints are noted in the appendix section of the retro-commissioning report through field observations and measurements of Boilers (B-1 & B-2), Chillers (CH-1 and CH-2), AHUs (AHU-1 and AHU-2), Packaged AC unit (RTAC-1), Heat Exchanger (HX-1) and Pumps (P-1, P-2 and P-3). Space temperature measurements are also recorded to verify the setpoints are in accordance with the CFR. It is verified that the operating schedules reflected major space occupancy patterns and the CFR.
Sensors | YES | RCM#2 All critical sensors AHUs, Packaged AC unit, Boilers and Chillers have been tested for proper calibration 10% of all monitoring sensors for AHUs, Packaged AC unit, Boilers and Chillers have been tested for proper calibration. Test results have been provided within the report integral to the functional performance testing. Gauge/control panel readings were compared against instrument measured readings and recommendations are made to calibrate/replace (if calibration is not possible) all monitoring sensors and all critical sensors that are found out of calibration by +/- 10%.
Simultaneous heating and cooling | NO | Based on testing of all major HVAC system air handling units (AHU-1 & AHU-2) no simultaneous heating and cooling is observed to be occurring. The air cooled chillers CH-1 & CH-2 are drained during the entire winter and the boilers B-1 & B-2 are manually shutdown during the entire summer.
Boilers tuned for optimal efficiency | YES | RCM#13 Steady state combustion efficiency tests were performed on Boiler B-1 and Boiler B-2 as per the amended rule of the LL87/09. The results from the combustion test performed on the boilers showed that the excess air percentage for boiler 1 and 2 was 50% and 60% respectively. Optimal excessive air percentage for natural gas boilers is approximately 15 - 20%. Mechanical contractor to clean tubes and tune burners for optimal steady state efficiencies on both boilers.
Manual override remediation | NO | As confirmed with the facility maintenance staff there is a protocol in place for the remediation of the issues causing manual overrides. No manual override on any base building major HVAC equipment has been observed. AHUs, Boilers and Chillers along with associated pumps and fans are observed to be operating on "AUTO" mode.
Leaks | YES | RCM#8 Each major equipment in the common areas and 10% of the equipment in the non-common tenant areas is visually checked for water, steam, oil or air leaks. Boilers (B-1 & B-2 )and all exposed steam piping, control valves and unions in the building were visually checked and verified for some major and minor leaks in the steam distribution system that are required to be fixed by the mechanical contractor.
1RCNY 103-07 f(2) HVAC and Service Water Distribution
Pipe insulation | YES | RCM#14 All exposed steam distribution and condensate return piping throughout the building was visually checked. It was estimated that 200 feet of exposed steam piping (average pipe size of 3 inches) in the basement had either partially deteriorated insulation or entirely uninsulated. Mechanical contractor to insulate all uninsulated/deteriorated piping in accordance with NYCECC, in effect at the time of installation.
High pressure steam traps | NOT APPLICABLE | Existing steam distribution system is a low pressure steam system. There is no high pressure steam trap in the facility.
One-pipe steam distribution | NOT APPLICABLE | "Steam and travel time test" is not required to be conducted on the existing distribution system. Existing distribution steam is not one-pipe steam distribution system.
Two-pipe steam distribution | YES | RCM#12 Existing major steam boilers produces steam that gets converted to HW supply via a heat exchanger. Building is not a two-pipe steam distribution system. "Differential temperature test" has not been conducted as it is not applicable on such system. However, steam traps (total 10 F&T traps) associated with the major equipment located in the common areas of the facility are tested for proper operation using ultrasonic leak detector and thermal imaging camera. 9 out of the 10 steam traps were not functioning properly and were determined to be at the end of useful lives. Mechanical contractor to repair or replace all 9 defective steam traps. Also, a new testing protocol is now developed and set in place for the facility maintenance staff to test and replace non-functional traps in future.
Air-side distribution | NO | All dampers, fans, actuators and controls associated with air-side distribution serving major equipment (AHU-1, AHU-2 and RTAC-1) are functionally tested for proper operation as per CFR. Completed functional performance test forms have been included in the retro-commissioning report. No deficiency is identified.
Water-side distribution | YES | RCM#5 All HW/CHW coils, valves, automatic isolation valves at pumps, actuators and controls serving AHU-1 and AHU-2 are functionally tested for proper operation as per CFR. Completed functional performance test forms have been included in the retro-commissioning report including the test results. Buidling owner to engage the HVAC contractor to repair the CHW/HW coil supply valves serving the AHU-1 and AHU-2. Opening and closing of the valves is not occuring in conjuction with the controls sequence of operation. HW/CHW valves are observed to not fully close or fully open resulting in leakage that is also causing simulataneous heating and cooling issues.
Domestic hot water system temperature settings | YES | RCM#7 The supply domestic hot water temperature is measured to be an average of 112 deg. F. The representative sample (10% of the non-common tenant areas) of measurements are taken using thermometer at the discharge of the bathroom and kitchen faucets to check compliance against the DHW delivery temperatures per the current facility requirements. The existing 3-way mixing/tempered valve needs to be adjusted/repaired by the mechanical contractor to ensure a delivery temperature of 120 deg. F to the apartments.
Mechanical ventilation rates | NO | Outside air (CFMs) intake for AHU-1, AHU-2 and RTAC-1 are measured using calibrated duct traverse/anemometer to confirm that the flow rates are appropriate for the current facility requirements (CFR). No correction is needed. Outside air for AHU-1 is measured at 8,458 CFM (within +/- 10% of CFR). RTAC-1 is a 100% outside air unit, the OA dampers were 100% open during the site visit. Measured outside airflow for RTAC-1 is 4,959 CFM (within +/- 10% of CFR). Measured outside airflow for AHU-2 is 6,235 CFM (within +/- 10% of CFR). CO2 measurements (in ppm) were also taken throughout the building. Ventilation rates are acceptable in all sampled three outdoor air intakes. See Appendix section in the retro-cx report for measured vs CFR values.
1RCNY 103-07 f(3) Lighting System
Light levels | YES | RCM#6 Lighting levels (foot candles) are measured using the calibrated light meter in all common areas served by the base building lighting system. Lighting level measurements revealed more than 90% of failures when compared to the CFR (based on applicable NYC building code, ASHRAE 90.1 and IESNA recommended lighting levels). A detail breakdown of pass / fail measurements results are noted in retro-cx report. Replacing non-functional and/or inefficient lamps in areas where lighting levels are lower is required to meet CFR lighting levels.
Sensors and controls | NO | Interior lighting in each space of the common area is controlled manually by ON/OFF toggle switches. There are no automatic controls/sensors for interior lighting. Majority of the exterior lighting is controlled by a time clock that is verified to be set up and functioning properly. All exterior lighting fixtures controlled by Photocell sensors are tested and verified to be functional properly.
1RCNY 103-07 f(4) Envelope
Sealants and weather-stripping | NO | A visual inspection is conducted in a sample set constituting all common areas and ten percent of all accessible locations in the non-common tenant areas to confirm that the weather-stripping and sealants installed around doors, windows, conduits, piping, joints and other areas of potential air infiltration are in good condition. No condition of missing sealants and/or weather-stripping is discovered. Photos are included in the report.
Windows and doors | NO | A visual inspection is conducted in all common areas to confirm that all windows and doors are in good condition. No broken window or exterior door is found during the walkthrough. Sample photos have been included in the retro-commissioning report.
1RCNY 103-07 f(5) Training and Documentation
Training of critical operations and maintenance staff | NO | Building maintenance staff is sufficiently equipped with appropriate documented material including but not limited to system operations manuals, maintenance manuals, specific sequence of operations, log books, manual over-ride protocols as well as deemed sufficiently trained to operate and maintain all base building systems in an optimal energy conservative manner. All expectations in how facility shall be maintained post retro-cx effort has been conveyed to the building staff. There is no need to recommend certain third party certifications/training to the building maintenance and operation staff based on the interviews conducted with the building staff.
Preventative maintenance schedules | NO | On-site documentation has been verified and noted on the retro-commissioning report. Preventative maintenance schedules, based on manufacturer’s guidelines, for all major equipment and sub-systems are already confirmed to exist at the facility and copies have been included in the retro-commissioning report.
Comments/Notes: (If Applicable)
Note that the building is 100% Multifamily building. There is no existence of non-common owner areas. Testing methodology and sampling is limited to major equipment located in all common areas and all such major equipment located on 10% of the non-common tenant areas.
Note on D8: If "YES" is selected for "Deficiency Identified", enter the associated RCM# matching with the RCM# in the "Correction" tab and the summary of testing methodology. If "NO" is selected for "Deficiency Identified", list the project specific information on major equipment, sub-equipment and components tested in common areas, non-common owner areas, and non-common tenant areas and the summary of the testing methodology adapted to arrive to the conclusion that there exist no deficiency as compared to the established CFR. Refer to the section within the retro-commissioning report for the details on the testing documentation. If "NOT APPLICABLE" is selected for "Deficiency Identified", provide a statement on the justification.

## Correction
RETRO-COMMISSIONING MASTER LIST OF FINDINGS
Retro-Commissioning Measures
RCM # | Retro-Commissioning Category | Sub Category | Measure Description and Summary of Deficiency Corrected | Status of Implementation | Provide explanation If the Status of Implementation is "In Progress" or "Not Applicable" | Deficiency Corrected (Date) | Deficiency verified by the Retro-cx agent as Corrected (Date) | By whom the correction was made | Actual cost ($) of Implementation | Annual Energy Savings based on Fuel Type |  |  |  |  | Total Annual Energy Savings (kBTU) | Annual Cost Savings ($) | Simple Payback (Years) | The Information in this tab is applicable to the following buildings:
[10 empty] | Electricity (kWh) | Natural Gas (Therms) | Fuel Oil (Gallons) | Steam (lb.) | Other Fuel Type (kBTU)
1 | HVAC and service water equipment | Temperature and pressure setpoints and setbacks | Temperature setpoints for the two major AHUs units (AHU-1 and AHU-2) in the common areas were adjusted to meet the current facility requirements (CFR). | Completed |  | 06/25/2020; 11/01/2020 | 44155 | XYZ Mechanical Services | 1000 | -2153 | 416 |  |  |  | 34253.964 | 236.46 | 4.229 | BIN(s)
2 | HVAC and service water equipment | Sensors | Calibrated OAT, MAT, RAT and enthalpy sensor for the rooftop packaged air conditioning unit. Replaced OAT, MAT and RAT sensors for the packaged air conditioning unit (RTAC-1) because calibration was not possible. | Completed |  | 43770 | 43789 | XYZ Mechanical Services | 2835 | [5 empty] | Not Quantifiable | N/A | #VALUE! | 0101010
3 | HVAC and service water equipment | Functional performance testing | 1) Adjusted settings on heat timer control panel for automatic control of the boilers to avoid manual bypassing and minimize excessive cycling. 2) Repaired malfunctioning sail switch in the basement controlling H&V-1 unit. | Completed |  | 43784 | 43789 | XYZ Mechanical Services | 3250 |  | 985 |  |  |  | 98500 | 1477.5 | 2.1997 | 0101011
4 | HVAC and service water equipment | Functional performance testing | Corrected outdoor reset function for the chillers CH-1 and CH-2 to meet the current facility required outdoor reset schedule. | Completed |  | 43666 | 43789 | HVAC Contractor, Inc | 2400 | 3840 |  |  |  |  | 13102.08 | 691.2 | 3.4722
5 | HVAC and service water distribution | Water-side distribution | Repaired the CHW/HW coil supply valves serving the AHU-1 and AHU-2. | Completed |  | 43631 | 43789 | ABC Contractors | 7000 | 6421 | 492 |  |  |  | 71108.452 | 1893.78 | 3.6963
6 | Lighting Systems | Light levels | Existing lamps within the lighting fixtures in the hallways, basement, laundry room, gym room and pool area were upgraded to high efficacy lamps. Lighting levels (foot-candles) for all such common areas were verified after the upgrade to meet the required current facility requirements (CFR) lighting levels. | Completed |  | 43692 | 43794 | In-House Maintenance Staff (approx. X hours spent; $/hr wage rate) | 3400 | [5 empty] | Not Quantifiable | N/A | #VALUE!
7 | HVAC and service water distribution | Domestic hot water system temperature settings | Adjusted DHW supply temperature to deliver a minimum of 120 deg. F as per the current facility requirements by adjusting the DHW control settings. | Completed |  | 43692 | 43794 | In-House Maintenance Staff (approx. X hours spent; $/hr wage rate) | 2200 | [5 empty] | Not Quantifiable | N/A | #VALUE!
8 | HVAC and service water equipment | Leaks | 1) A continuous major live steam leak from the top (plugged steam outlet) of Boiler B-2 was fixed. This was the major leak fixed while few minor leaks were also fixed in steam supply piping/valves at various locations in the basement including leaky condensate return piping at the joints/fittings. 2) Steam leaking from dielectric connections to H&V-1 steam coils was fixed. Gaskets were replaced. | Completed |  | 43723 | 43794 | ABC Contractors | 1500 |  | 1986 |  |  |  | 198600 | 2979 | 0.50352
9 | HVAC and service water equipment | Pre-testing verification | 1) DX cooling coils on all AHU-1 thru 2 that were inspected to be loaded with dirt were cleaned. 2) Dirty and clogged outdoor air and return air intakes for all AHUs were cleaned. | Completed |  | 7/15//2019 | 43794 | ABC Contractors | 550 | 1015 |  |  |  |  | 3463.18 | 182.7 | 3.0104
10 | HVAC and service water equipment | Pre-testing verification | Existing dirty filters for AHU-1, AHU-2, and RTAC-1 were replaced with new filters. | Completed |  | 43570 | 43794 | In-House Maintenance Staff (approx. X hours spent; $/hr wage rate) | 2200 | 2400 |  |  |  |  | 8188.8 | 432 | 5.0926
11 | HVAC and service water equipment | Pre-testing verification | Loose flat fan belt for AHU-1 was tightened to avoid excessive slippage and broken belt of AHU-2 was replaced with new. | Completed |  | 43600 | 43794 | ABC Contractors & Retro-Commissioning Agent | 1500 | 4400 |  |  |  |  | 15012.8 | 792 | 1.8939
12 | HVAC and service water distribution | Two-pipe steam distribution | All of the existing steam traps in common areas serving the heat exchanger were replaced with new. There are no steam traps in the non-common owner areas or non-common tenant areas of the facility. | Completed |  | 43344 | 43424 | ABC Contractors & Retro-Commissioning Agent | 14500 |  | 1876 |  |  |  | 187600 | 2814 | 5.1528
13 | HVAC and service water equipment | Boilers tuned for optimal efficiency | 1) Cleaned tubes/heat exchanger surfaces on both scotch marine boilers B-1 & B-2 2)Tuned Burners for B-1 and B-2 to operate at optimal efficiencies at both high and low firing rates. See appendix G of the retro-commissioning report for a copy of the post tuned test results. 3) Replaced damper switches and actuators for two combustion air intake dampers supplying combustion air to the boiler room. | Completed |  | 43388 | 43424 | ABC Contractors | 2600 |  | 623 |  |  |  | 62300 | 934.5 | 2.7822
14 | HVAC and service water distribution | Pipe insulation | Insulated all exposed (uninsulated/deteriorated insulation) steam supply piping (3 inches and greater) in the common areas as per the NYCECC, in effect at the time of the installation. | Completed |  | 43388 | 43424 | In-House Maintenance Staff (approx. X hours spent; $/hr wage rate) | 2200 |  | 178 |  |  |  | 17800 | 267 | 8.2397
15 | [16 empty] | #DIV/0!
16 | [16 empty] | #DIV/0!
17 | [16 empty] | #DIV/0!
18 | [16 empty] | #DIV/0!
19 | [16 empty] | #DIV/0!
20 | [16 empty] | #DIV/0!
21 | [16 empty] | #DIV/0!
22 | [16 empty] | #DIV/0!
23 | [16 empty] | #DIV/0!
24 | [16 empty] | #DIV/0!
25 | [16 empty] | #DIV/0!
[9 empty] | 47135 | 15923 | 6556 |  |  |  | 709929.276 | 12700.14 | 3.7114
Comments/Notes (if applicable):
Note on E9: Department of Buildings: Summary of methodology of correction adopted. List, quantify and describe all associated items adjusted, calibrated, balanced, repaired, replaced, installed, insulated, tuned or cleaned.
Note on Q9: Department of Buildings: Sum of annual electricity, natural gas, fuel oil, steam and other fuel type in common units (kBTU)

## DropDowns (hidden)
LT_Boro | LT_FilStat | LT_Typ | LT_ProfTyp | LT_CertTyp1 | Space Types | Metering Configuration | LT_OperCert | System Designation | Heating Equip. Type | Equipment Location | Spaces Served | Fuel Source | Efficiency Units | Venting Type | Burner Equip. Type | Heating Distribution Types | Heating Terminal Equip. Type | Cooling Equipment Type | Air or Water Cooled | Cooling Efficiency Units | DHW Equipment Types | DHW from Space Heating Boiler | Roof Pitch | Ventilation Conditioned Supply | Ventilation System Operational | Windows Framing Material | # of Panes | Glass Coating | ECM Categories | ECMs_Conveying Systems | ECMs_Cooling System | ECMs_Distribution System | ECMs_Domestic Hot Water | ECMs_Envelope | ECMs_Fuel Switching | ECMs_Heating System | ECMs_HVAC Controls and Sensors | ECMs_Lighting | ECMs_Motors | ECMs_On-Site Generation | ECMs_Process/Plug Loads | ECMs_Submetering | ECMs_Ventilation | ECMs_Non-Base Building | ECMs_NonBaseBuildingCategories | ECM Recommendations | LT_RCMComp | LT_DEFID
Manhattan | Initial Filing | Yes | PE | Certified Commissioning Professional certified by the Building Commissioning Association | Bank/Financial Institution | Tenants directly metered | BOC | Primary | Air Source Heat Pump | Below Ground | 100% - 75% | Natural Gas | AFUE | Condensing | Full Modulation - Set to Manual | Electric | Baseboard | Absorption Chiller - 1 Stage | Air Cooled | SEER | Loop through Heating Boiler | Yes - Year Round | > 2:12 | No | Yes | Aluminum | Single | Heat Absorbing Tints | Conveying_Systems | Add Elevator Regenerative Drives | Add economizer cycle | Capture and return condensate | Decrease DHW Temperature | Add Window Films | #2 oil to natural gas | Add static pressure control | Change Set Points / Setbacks - Cooling | Delamp | Install VFDs | Install Cogeneration Plant | Automatic Shutdown / Sleep Mode for Computers | Install Submetering | Convert CV system to VAV type system | Appliances - Replace Air Conditioners | Non-Base Building | Recommended | YES | YES
Brooklyn | Amended Filing | No | RA | Certified Building Commissioning Professional certified by the AEE | Courthouse | Tenants sub-meterd by building owner | BPI | Secondary | Combined Heat and Power | Ground Level | 75% - 50% | #2 Oil | Et | Near-Condensing | Full Modulation - Set to Modulated | Forced Air | Radiator | Absorption Chiller - 2 Stage | Water Cooled | EER | Separate Hot Water Boiler with Storage Tank | Yes - Heating Season only | <2:12 | Yes - MAU | No | Wood | Single w/Storm | Reflective Coating | Cooling_System | Upgrade Controls | Add or upgrade cooling tower | Install or Upgrade Master Venting | Install DHW Controls | Exterior Door Replacement | #6 oil or #4 oil to #2 oil | Clean & Tune Boiler/Furnace | Change Set Points / Setbacks - Heating | Install Bi-level Lighting | Remove Motors | Install Ground Source Heat Pump | Data Center - Hot aisle/cold aisle design | Other | Install CAR Dampers | Appliances - Replace Dishwashers |  | Further Study Recommended | N/A | NO
Queens |  |  | Approved Agent | Existing Building Commissioning Professional as certified by the AEE | Data Center | Tenants not directly metered or sub-metered | Other | Tertiary | Electric Resistance | Above Ground | 50% - 25% | #4 Oil | HSPF | Forced Draft | Step Modulation | 1-pipe Steam | Fan Coil | Gas Engine Chiller | N/A | COP | Heat Exchanger from Heating System | No |  | Yes - ERV / HRV | Yes, but not used | Fiberglass | Double | Low-E Coating | Distribution_System | Upgrade Motors | Heat recovery - Cooling only | Insulate Ducts | Install Low-Flow Aerators | Increase insulation - Basement/Crawl Space | #6 oil or #4 oil to natural gas | Electric to Gas Conversion | Implement Static Pressure Reset | Install Occupancy/Vacancy Sensors | Upgrade Motors | Install Solar/Photovoltaic | Data Center - Other |  | Install Demand Control Ventilation | Appliances - Replace Refrigerators |  | Not Recommended |  | NOT APPLICABLE
Bronx |  |  |  | Commissioning Process Management Professional certified by ASHRAE | Hospital |  |  |  | Furnace |  | 25% - 0% | #6 Oil | COP | Atmospheric | Hi-Lo Operation | 2-pipe Steam | Duct | Electric Chiller |  | kW/Ton | Direct Fired Storage Tank |  |  | Yes - Economizer |  | Other | Triple | None | Domestic_Hot_Water | Other | Install VSD on Electric Centrifugal Chillers | Insulate Pipes | Install Low-Flow Showerheads | Increase insulation - Floor | #6 to dual fuel | Electric to Hydronic Conversion | Install Indoor Sensors | Install Photocell Control | Other | Other | Data Center - Server Virtualization |  | Install Exhaust Fan Timers | Appliances - Replace Washer / Dryer |  | Implemented
Staten Island |  |  |  | Accredited Commissioning Process Authority Professional approved by the University of Wisconsin | Hotel |  |  |  | Gas fired Packaged Terminal Units |  |  | Dual Fuel |  | N/A | On/Off | Hydronic | Radiant Floor | Window A/C |  |  | Instantaneous (Point of Use) | [6 empty] | Unknown | Envelope |  | Replace Chiller | Repair Leaks | Install Solar Thermal DHW | Increase insulation - Roof | District steam to on-site generation | Electric to Steam Conversion | Install or Upgrade EMS/BMS | Install Timers |  |  | Data Center - Upgrade Servers |  | Upgrade Exhaust Fans | Upgrade Lighting to Fluorescent
|  |  |  | Certified Commissioning Authority certified by the Associated Air Balance Council Commissioning Group | House of Worship |  |  |  | Gas Fired Rooftop Unit |  |  | Distric Steam |  |  | N/A | Vacuum Steam | PTAC | Through Wall A/C |  |  | Solar Thermal | [6 empty] | Other | Fuel_Switching |  | Upgrade Chiller | Replace or repair Main Steam Trap | Install Water Pressure Booster | Increase insulation - Wall | Utility steam to on-site generation | Heat recovery - Heating only | Install Programmable Thermostats | Replace Diffusers |  |  | Drain Water Heat Recovery |  | Upgrade Fan/Air Handlers | Upgrade Lighting to LED
|  |  |  | Building Commissioning Professional certified by ASHRAE | K-12 School |  |  |  | Ground Source Heat Pump |  |  | Electric |  |  |  |  | Other | PTAC |  |  | Other | [7 empty] | Heating_System |  | Replace packaged units | Replace or repair Steam Traps | Insulate DHW Piping | Install Cool or Green Roof | Other | Heat recovery from Utility Steam | Install TRVs | Upgrade Exit Signs to LED |  |  | Replace Clothes Dryers |  | Other | Other
|  |  |  | Commissioning Process Professional certified by NEBB | Medical Office |  |  |  | Hot Water Boiler |  |  | Propane | [5 empty] | Ductless Mini Split System | [10 empty] | HVAC_Controls_and_Sensors |  | Upgrade packaged units | Replace or repair Vacuum Pump | Insulate DHW Tank | Replace Curtain/Window Wall |  | Install Barometric Damper | Pneumatic to DDC conversion | Upgrade Exterior Lighting |  |  | Replace Washing Machines
|  |  |  | Technical Retro-Commissioning Professional certified by NEBB | Office |  |  |  | Steam Boiler |  |  | Other | [5 empty] | Split System Central Air | [10 empty] | Lighting |  | Other | Replace PTACs | Replace Piping | Replace Glazing and Frames |  | Install Bleeders | Replace Outdoor Reset | Upgrade to Fluorescent |  |  | Other
|  |  |  | Building Systems Commissioning Professional certified by NEBB | Residence Hall/Dorm |  |  |  | Distric Steam | [8 empty] | Steam Turbine Chiller | [10 empty] | Motors |  |  | Upgrade PTACs | Replace Tankless Coil | Replace Windows |  | Install Circulators | Zone control upgrades | Upgrade to LED
[5 empty] | Retail |  |  |  | Utility Steam | [8 empty] | DX Units | [10 empty] | On_Site_Generation |  |  | Seal Ducts | Separate DHW from Heating | Sealing - Door |  | Install Thermostatic Damper | Other | Other
[5 empty] | Senior Care Facility |  |  |  | Water Source Heat Pump | [8 empty] | Rooftop Units | [10 empty] | Process_and_Plug_Loads |  |  | Upgrade Pumps | Upgrade DHW Boiler | Sealing - Roof Penetrations |  | Insulate Condensate Tank
[5 empty] | Supermarket/Grocery | [12 empty] | Geothermal | [10 empty] | Submetering |  |  | Other | Other | Sealing - Room AC |  | Replace Boiler
[5 empty] | Warehouse | [12 empty] | Thermal Storage | [10 empty] | Ventilation |  |  |  |  | Sealing - Vertical Shafts |  | Upgrade Boiler
[5 empty] | Multifamily | [12 empty] | Water Side Economizer | [15 empty] | Sealing - Windows |  | Replace Boiler Jacket
[5 empty] | Other | [12 empty] | Other | [15 empty] | Other |  | Replace Burner
Upgrade Burner
Replace Furnace
Upgrade Furnace
Replace Steam Control Valves
Replace Steam Header
Steam to Hydronic Conversion
Other

## Dropdown List (hidden)
Categories | HVACandservicewaterequipment | HVACandservicewaterdistribution | LightingSystems | Envelope | Traininganddocumentation | StatusofImplementations
HVAC and service water equipment | Pre-testing verification | Pipe insulation | Light levels | Sealants and weather-stripping | Training | Completed
HVAC and service water distribution | Functional performance testing | High-pressure steam traps | Sensor controls | Windows and doors | Documentation | In Progress
Lighting Systems | Temperature and pressure setpoints and setbacks | One-pipe steam traps |  |  |  | Not Applicable
Envelope | Sensors | Two-pipe steam distribution
Training and Documentation | Simultaneous heating and cooling | Air-side distribution
| Boilers tuned for optimal efficiency | Water-side distribution
| Manual Overrides | Domestic hot water system temperature settings
| Leaks | Mechanical ventilation rates
Envelope | Sealants and weather-stripping