## Com.ECC - Envelope
2025 NYCECC Tabular Analysis Commercial Building - Envelope
Energy Code Scope of Work - Climate Zone 4
Job # | xxxxxxxxx | DOBNOW Job Type: | e.g. NB, Alt-CO, Alteration | DOB NOW Work Type: | e.g. I-1/GC- , P-2/ MS, PL
Filing Scope of Work |  | Enter PW-1 Scope of Work. Provide additional information and detailed description of Energy Code related work included in this Tabular Analysis
Note for ALTERATION job application: For each altered element where ALTERATION-specific exception/allowance is applied, edit the applicable row in the Proposed Design Value to cite the code section and to report the Supporting Documentation location. For examples of ALTERATION-specific exceptions/allowances, refer to 101.2.5 and C503.1
Does the alteration Scope of Work constitute: A Change of Use to the Building or any of the Spaces __________ or A major modification to the HVAC System(s).___________ For all ALTERATION job applications where the proposed scope of alteration work is limited to partial areas of the existing buildings and/or conditions, please provide a detailed description of the Area of Work, Proposed scope of work and itemize the specific altered elements in the tabular format below.
Professional Statement: "To the best of my knowledge, belief and professional judgment, this application is in compliance with the 2025 New York City Energy Conservation Code |  |  |  |  | Chapter C4 or NYC ASHRAE 90.1 "
NYCECC Citation | Provision | Item Description | Code Prescriptive Value (ECC) | Proposed Design Value | Supporting Documentation | Code Compliance
ENVELOPE REQUIREMENTS
C303 ASHRAE 4.1 | Materials, Systems & Equipment | Materials, systems and equipment shall be identified. | All materials listed in C303 shall be labeled, detailed or verified in a manner that will allow a determination of compliance with the applicable provisions of this code. | The type, thickness, spacing and rated value of all materials, systems and/or equipment has been identified in the construction documents Y/N. | Drawing Notes on plan A-xx, A-xx and specifications on drawing A-xx | COMPLIES or NOT APPLICABLE
C401.3 | Envelope Certificate | A permanent building thermal envelope certificate shall be completed by an approved party. Such certificate shall be posted on a wall in the space where the space conditioning equipment is located, a utility room or other approved location | A copy of the certificate shall also be included in the construction files for the project. The certificate shall include the following: 1. R-values of insulation installed in or on ceilings, roofs, walls, foundations and slabs, basement walls, crawl space walls, floors and ducts outside conditioned spaces. 2. U-factors and SHGC of fenestrations. 3. Results from any building thermal envelope air leakage testing performed on the building. | The Permanent Certificate provided as per code requirements is located (sample text by applicant) | Certificate note located on plan A-xx and specifications on drawing A-xx | COMPLIES or N/A
C402.1.1 | Low Energy Buildings | Low-energy buildings defined as greenhouses and equipment buildings may be exempt from envelope provisions | Low-energy buildings, or portions thereof, separated from the remainder of an otherwise conditioned building by building thermal envelope assemblies, shall be exempt from the building thermal envelope provisions of Section C402 where one of the following is met: 1. Those with a peak design rate of energy usage less than 3.4 Btu/h × ft2 (10.7 W/m2 ) or 1.0 watt per square foot (10.7 W/m2 ) of floor area for space conditioning purposes. 2. Those that do not contain conditioned space. | Application meets the requirements for a low-energy building by demonstration of (sample statement supporting C402.1.1 (1) or C402.1.1.(2) | Low energy Building Notes on plan A-xx, A-xx and specifications on drawing A-xx | COMPLIES or N/A
C402.1.1.1 | Low Energy Buildings - Greenhouses | Greenhouses that are mechanically heated or cooled and do not meet the provisions for low-energy buildings in Section C402.1.1 shall be exempt from the building thermal envelope provisions of Section C402 where all the following are met: | 1. Exterior opaque envelope assemblies comply with Sections C402.2 and C402.5.5. 2. Interior partition building thermal envelope assemblies that separate the greenhouse from conditioned space comply with Sections C402.2, C402.5.3 and C402.5.5. 3. Fenestration assemblies that comply with the requirements in Table C402.1.1.1. The U-factor for a roof shall be for the roof assembly or a roof that includes the assembly and an internal curtain system. | Greenhouse meets the requirements for a low-energy building by demonstration of (sample statement supporting C402.1.1.1 (1), C402.1.1.1(2) and C402.1.1..1(3) with R-values and U-factors indicated | Greenhouse Building Notes on plan A-xx, A-xx and specifications on drawing A-xx | COMPLIES or N/A
C402.1.1.2 | Low Energy Equipment Buildings | Equipment Buildings that comply with all the following shall be exempt from the building thermal envelope provisions of this code: | 1. Are separate buildings with not more than 1,200 square feet (111 m2 ) of floor area. 2. Are intended to house electric equipment with installed equipment power totaling not less than 7 watts per square foot (75 W/m2 ) and not intended for human occupancy. 3. Have a heating system capacity not greater than 20,000 Btu/h (6 kW) and a heating thermostat setpoint that is restricted to not more than 50°F (10°C). 4. Have an average wall and roof U-factor less than 0.2 in Climate Zones 4 ... 5. Comply with the roof solar reflectance and thermal emittance for Climate Zone 1. | Equipment Building meets the requirements for a low-energy exemption by demonstration of: 1. Area of xx gross square feet 2. Installed equipment = xx watt/s.f 3. Heating capacity = xx Btuh with setpoint at xx deg. F. 4. Average Factor = U-0.xx 5. Solar reflect. /emit. = xx | Equipment Building Notes on plan A-xx, A-xx and specifications on drawing A-xx | COMPLIES or N/A
ENVELOPE COMPONENTS
Tables C402.1.2 & 402.1.3 Table 5.5-4 |  |  | Maximum U-factors or combined R-Values ca = cavity insulation ci = continuous insulation
ROOF | Insulation entirely above roof deck | Continuous Insulation U-factor when entirely above roof deck | Group R = 0.080 or R15ci ( when on exterior) or 20 ci | Insulation rated R-value = ( R-value). noted with minimum & maximum thickness, if tapered) | Drawing Notes on plan A-xx, A-xx and specifications on drawing A-xx | COMPLIES or N/A
ROOF | Pre-Engineered metal buildings ) | R-value applies when thermal spacer block is provide. | 0.035 or R19ca +R11 Liner System | Frame depth = (e.g W26 or truss) Purlin depth = xx Insulation rated R-value = R= xx Liner system value = R =- xx | Drawing Notes on plan A-xx, A-xx and specifications on drawing A-xx | COMPLIES or N/A
ROOF | Ceiling Insulation values | Ceiling U-factor or R-value when insulation is located uncompressed in cavity on the entire ceiling (See C402.2.1) | 0.020 or R53ca | Joist depth = ( sample text e.g 2x12 or C12 steel joist) Insulation rated R-value = ( R-value) | Drawing Notes on plan A-xx, A-xx and specifications on drawing A-xx | COMPLIES or N/A
WALLS, above grade | Mass Walls | CMU or Concrete wall values per C402.1.3.4 | Group R = 0.080 or R13.3ci All Other = 0.090 or R13.3ci | Continuous R -value = R-xx on exterior or R-xx on interior | Drawing Notes on plan A-xx, A-xx and specifications on drawing A-xx | COMPLIES or N/A
WALLS, above grade | Pre-Engineered metal buildings ) | R-value applies for insulation at wall girts | 0.048 or R13ca + R14.9ci | Frame depth = (e.g frame leg depth Wall girt depth = xx Cavity Insulation value = R= xx Continuous Insul. value = R = xx | Drawing Notes on plan A-xx, A-xx and specifications on drawing A-xx | COMPLIES or N/A
WALLS, above grade | Metal framed (CFS) Walls | Metal framed wall values | 0.061 or R13ca + R 8.5 ci *Alternate Calculations shall be determined in accordance with 2025 NYC ASHRAE, Appendix A | Stud depth & spacing = ( 6" CFS @16") Cavity R-value = ( Type & R-value) Continuous R -value ( R-value) | Drawing Notes on plan A-xx, A-xx and specifications on drawing A-xx | COMPLIES or N/A
WALLS, above grade | Wood framed Walls | Wood framed wall values | 0.061 or R13ca + R 4.5ci or R19ca + R1.5ci | Stud depth & spacing = (2x6 @ 16") Cavity R-value = ( Type & R-value) Continuous R -value ( R-value) | Drawing Notes on plan A-xx, A-xx and specifications on drawing A-xx | COMPLIES or N/A
WALLS, below grade | Below Grade Walls at Basement & Cellar | Mass Foundation Wall, & other below grade walls adjacent to earth with values per C402.1.3.4. ( basement, crawls or cellar) | Group R = C-0.092 or R10ci All Other = C-0.119 or R7.5ci | Continuous R -value ( R-value) * Provide calculations if ca with steel studs is used (C-factor) | Drawing Notes on plan A-xx, A-xx and specifications on drawing A-xx | COMPLIES or N/A
FLOORS | Mass Floor | Concrete floor or slab with values per C402.1.3.4 | Group R = 0.051 or R 16.7ci All Other = 0.057 or R 14.6ci | Continuous R -value = R-xx below slab or R-xx above slab | Drawing Notes on plan A-xx, A-xx and specifications on drawing A-xx | COMPLIES or N/A
FLOORS | Framed Floors | Wood or Steel framed joists | 0.033 or R30ca | Joist depth & spacing = ( 2x12 @16") Insulation rated R-value = ( R-value) | Drawing Notes on plan A-xx, A-xx and specifications on drawing A-xx | COMPLIES or N/A
FLOORS | Slab-on-grade floors (Unheated) | Mass Slab, directly over earth, typically less than 4 feet below grade | F- 0.52 or 15ci to 24" below grade | Edge R-value = (R-value & depth) Under slab R -value ( R-value) | Drawing Notes on plan A-xx, A-xx and specifications on drawing A-xx | COMPLIES or N/A
FLOORS | Slab-on-grade floors (Heated) | Mass Slab, directly over earth, typically less than 4 feet below grade | F- 0.62 or 20ci to 48" below grade + R 5ci under entire slab | Edge R-value = (R-value & depth) Under slab R -value ( R-value) |  | COMPLIES or N/A
C402.5 5.5.4 | FENESTRATION | Fenestration shall comply with Sections C402.5.1 through C402.5.5 and Table C402.5 or ASHRAE 5.5.4.
C402.5.1 C402.5.1.2 | Maximum Fenestration Areas | Maximum Fenestration Areas not including opaque doors and Spandrels | Fenestration Area = 30 percent of gross above grade wall area with Skylight Area = 3 percent of gros roof area. | Window/Wall Area = xx percent Skylight Area = xx percent Increased area is applied by specification of ( describe daylight responsive controls) | Drawing Notes on plan A-xx, A-xx and specifications on drawing A-xx | COMPLIES or N/A
5.5.4.2.1 | Maximum Fenestration Areas | Maximum Fenestration Areas not including opaque doors and Spandrels | Fenestration Area = 40 percent of gross above grade wall area with Skylight Area = 3 percent of gros roof area. | Window/Wall Area = xx percent Skylight Area = xx percent Increased area is applied by specification of ( describe daylight responsive controls) | Drawing Notes on plan A-xx, A-xx and specifications on drawing A-xx | COMPLIES or N/A
Table C402.5 Table 5.5-4 FIXED WINDOWS | Metal Framed Vertical Fenestration | Vertical Fenestration U-factor | 0.30 below 95' , 0.34 above 95' | Fixed Unit U value Below 95' Fixed Unit U value Above 95' | Schedule on plan A-xx, A-xx and details on drawing A-xx | COMPLIES or N/A
Table C402.5 Table 5.5-4 OPERABLE WINDOWS & DOORS | Metal Framed Vertical Fenestration | Vertical Fenestration U-factor | 0.40 below 95' , 0.42 above 95' | Operable Unit U value Below 95' Operable Unit U value Above 95' | Schedule on plan A-xx, A-xx and details on drawing A-xx | COMPLIES or N/A
Table C402.5 Table 5.5-4 WINDOWS & DOORS | Non- Metal Framed Vertical Fenestration | Vertical Fenestration U-factor | 0.40 below 95' or above 95' (includes wood-framed clad units, vinyl framed units, UPVC units or composite units) | Non-Metal Frame U value | Schedule on plan A-xx, A-xx and details on drawing A-xx | COMPLIES or N/A
Table C402.5 Table 5.5-4 ENTRANCE DOORS | Fenestration | Vertical Fenestration U-factor | 0.63 | U value | Schedule on plan A-xx, A-xx and details on drawing A-xx | COMPLIES or N/A
C402.5.3 Tbl 5.5.4.4.1 | Projection Factor < 0.2 | Fenestration SHGC | 0.33 | Projection Factor = value SHGC = value | Schedule on plan A-xx, A-xx and details on drawing A-xx | COMPLIES or N/A
C402.5.3 Tbl 5.5.4.4.1 | Projection Factor < 0.2 PF < 0 .5 | Fenestration SHGC | 0.40 | Projection Factor = value SHGC = value | Schedule on plan A-xx, A-xx and details on drawing A-xx | COMPLIES or N/A
C402.5.3 Tbl 5.5.4.4.1 | Projection Factor > 0.5 | Fenestration SHGC | 0.53 | Projection Factor = value SHGC = value | Schedule on plan A-xx, A-xx and details on drawing A-xx | COMPLIES or N/A
Table C402.5 Table 5.5-4 | Skylight | Skylight U-factor | 0.48 | U value | Schedule on plan A-xx, A-xx and details on drawing A-xx | COMPLIES or N/A
C402.5.3.1 5.5.4.4.2 | Skylight SHGC | Skylight SHGC | 0.38 | SHGC = value | Schedule on plan A-xx, A-xx and details on drawing A-xx | COMPLIES or N/A
C402.6, 5.4.3. | AIR LEAKAGE | The building thermal envelope shall comply with Sections C402.6.1 through C402.6.7. or ASHRAE 5.4.3.
C402.6 C402.6.1 5.4.3.2. | Installation of the continuous air barrier | The building thermal envelope shall comply with Sections C402.6.1 through C402.6.7 or ASHRAE 5.4.3.2 | A continuous air barrier shall be provided throughout the building thermal envelope. The air barrier is permitted to be located at any combination of inside, outside or within the building thermal envelope. The air barrier shall comply with Sections C402.6.1.1 and C402.6.1.2. or ASHRAE 5.4.3.2. | A continuous air barrier shall be provided by = ( describe materials and applications that proved continuity of thermal envelope air barrier.) | Narrative and specifications on drawing EN-xx | COMPLIES or N/A
C402.6.1.1 5.8.3.1 | Air barrier design and documentation requirements | Design of the continuous air barrier shall be documented as follows: | 1. Components comprising the continuous air barrier and their position within each building thermal envelope assembly shall be identified. 2. Joints, interconnections and penetrations of the continuous air barrier components shall be detailed. 3. The continuity of the air barrier building element assemblies that enclose conditioned space or provide a boundary between conditioned space and unconditioned space shall be identified. 4. Documentation of the continuous air barrier shall detail methods of sealing the air barrier, such as wrapping, caulking, gasketing, taping or other approved methods at the following locations: 4.1. Joints around fenestration and door frames. 4.2. Joints between walls and floors; between walls at building corners; between walls and roofs, including para-pets and copings; where above-grade walls meet foundations; and at similar intersections. 4.3. Penetrations through the continuous air barrier. 4.4. Building assemblies used as ducts or plenums. 4.5. Changes in continuous air barrier materials/assembly | 1. Components of continuous air barrier are located describe location & material. 2. Joints, interconnections and penetrations are sealed with describe locations & material. 3. Air barrier element assemblies that enclose conditioned space or provide a boundary between conditioned and unconditioned space are describe locations & material.. 4. Wrapping, caulking, gasketing, taping or other methods for joints, penetrations and ducts are provide by: describe methods &material | Drawing details on plan/ section A-xx, A-xx , Schedule of Inspections on EN-xx and material specifications on drawing A-xx | COMPLIES or N/A
C402.6.1.1 C402.6.1.2 5.9.1 | Air barrier Testing and Inspections | Testing and Inspection of the continuous air barrier shall be documented as follows: | 5. Identify where testing will or will not be performed in accordance with Section C402.6.2. or 5.9.1. Where testing will not be performed, a plan for field inspections required by Section C402.6.2.3 or 5.9.1.2 shall be provided that includes the following: 5.1. A schedule for periodic inspection. 5.2. The continuous air barrier scope of work. 5.3. A list of critical inspection items. 5.4. Inspection documentation requirements. 5.5. Provisions for corrective actions where needed | 5. Identify where testing will or will not be performed in accordance with Section C402.6.2. In areas where testing will not be performed, field inspections shall be provided by: 5.1. Periodic inspections per RCNY 5000-01 ITEM xx 5.2. Continuous inspections per RCNY 5000-01 ITEM xx 5.3. A list of critical inspection items is located in ( describe location of Table or narrative). 5.4. Inspections will be documented by ( responsible party) 5.5. Provisions for corrective actions will be provided by (responsible party) | Drawing details on plan A-XXX, A-xx ,Narrative and/or Schedule of Inspections on EN-xx and specifications on drawing A-XXX | COMPLIES or N/A
C402.6.2 5.4.3.1.4 | Air Leakage Compliance - Testing | Air leakage of the building thermal envelope shall be tested by an approved third party in accordance with Section C402.6.2.1, C402.6.2.2 or 5.4.3.1.4 | The measured air leakage shall not be greater than 0.35 cubic feet per minute per square foot (1.0 L/s x m2) of the building thermal envelope area at a pressure differential of 0.3 inch water gauge (75Pa) with the calculated building thermal envelope surface area being the sum of the above- and below-grade building thermal envelope. | Whole building thermal envelope testing to be in accordance with ASTM E 779, ASTM E1827, ASTM E3158 or an equivalent approved method. EXCEPTION IS ALLOWED FOR (describe exception and alternative methodology) | Narrative describing testing methodology with diagram of gross cubic feet of area to be tested is located on EN-xx | COMPLIES or N/A
C402.6.2.2 5.7.3.1 | Building thermal envelope design and construction verification criteria | The installation of the continuous air barrier shall be verified by a registered design professional or Approved agency in accordance with: | 1. A review of the construction documents and other supporting data shall be conducted to assess compliance with the requirements in Section C402.6.1 or 5.7.3.1 2. Inspection of continuous air barrier components and assemblies shall be conducted during construction to verify compliance with the requirements of Section C402.6.2.2.1, C402.6.2.2.2 or 5.7.3.1 The air barrier shall remain accessible for inspection and repair. 3. A final inspection report shall be provided for inspections completed by the registered design professional or approved agency. The inspection report shall be provided to the building owner or owner’s authorized agent and the building official. The report shall identify deficiencies found during inspection and details of corrective measures taken. | A narrative describing inspection requirements, including inspections to be performed and locations required shall be provided. Testing procedures for areas described above shall be performed by ( describe inspection type, ( visual, measured, smoke, infrared, etc.) , timing and frequency of inspections and specific areas to be verified. | Narrative describing testing methodology with diagram of areas to be tested is located on EN-xx | COMPLIES or N/A
C402.6.3 Table C402.6.3 Table 5.8.3.2 | Air Leakage of Fenestration & Opaque Doors | Fenestration Air Leakage rates | ASSEMBLY MAXIMUM LEAKAGE RATE(cfm) All Windows & Doors 0.20 cfm/ft2 Skylights with weeps 0.30 cfm/ft2 Skylights ( all others) 0.20 cfm/ft2 Curtain Walls & Storefronts 0.06 cfm/ft2 Entrance & Revolving Doors 1.00 cfm/ft2 Power Operated Sliding Doors 1.00 cfm/ft2 Rolling Doors 1.00 cfm/ft2 Garage Doors 0.40 cfm/ft2 High Speed Doors 1.30 cfm/ft2 | ASSEMBLY MAX.LEAKAGE RATE(cfm) Windows & Doors 0.xx cfm/ft2 Skylights with weeps 0.xx cfm/ft2 Skylights ( all others) 0.xx cfm/ft2 Curt.Walls & Storefronts 0.xx cfm/ft2 Entrance & Rev. Doors 1.xx cfm/ft2 Power Oper. Sliding Drs 1.xx cfm/ft2 Rolling Doors 1.xx cfm/ft2 Garage Doors 0.xx cfm/ft2 High Speed Doors 1.xx cfm/ft2 | Drawing details on plan A-xx, A-xx ,Narrative and/or Schedule of Inspections on EN-xx and specifications on drawing A-xx | COMPLIES or N/A
C402.6.4 C402.6.5 C402.6.6 C402.6.7 5.4.3.3 5.5.3.4 | Building Doors, Access openings, Stairways, Elevator lobbies, Shafts, Vestibules and Loading dock weather seals | Gaskets, Self-closing devices and weather seals that restrict air leakage | C402.6.4 Doors and access openings from conditioned space to shafts, chutes, stairways and elevator lobbies not within the scope of the fenestration assemblies covered by C402.6.3 shall be gasketed, weather-stripped or sealed. C402.6.5 Stairway enclosures, elevator shaft vents and other outdoor air intakes and exhaust openings integral to the building thermal envelope shall be provided with dampers per Section C403.7.7. C402.6.6 Vestibules. Building entrances shall be protected with an enclosed vestibule. Doors opening into and out of the vestibule equipped with self-closing devices. Vestibules shall be designed so that in passing through the vestibule it is not necessary for the interior and exterior C402.6.7 Cargo door openings and loading door openings shall be equipped with weather seals that restrict air leakage and provide direct contact along the top and sides of vehicles. | Doors and access openings from conditioned space to shafts, chutes, stairways and elevator lobbies shall be gasketed, weather-stripped or sealed with (describe ) Stairway enclosures, elevator shaft vents and other outdoor air openings shall be provided with (describe dampers) Vestibules. Building entrances shall be protected with an enclosed vestibule. Vestibule provided ( describe location ) Cargo and loading door openings shall be equipped with weather seals (describe type & location) | Drawing details on plan A-XXX, A-xx ,Narrative and/or Schedule of Inspections on EN-xx and specifications on drawing A-XXX | COMPLIES or N/A
C402.7 5.5.5 | THERMAL BRIDGES | Where present, intersections listed in Section C402.7.1 or 5.5.5 that create thermal bridges shall be detailed in construction documents. Thermal bridges shall be mitigated in accordance with Section C402.7.2 or 5.5.5 , with exceptions for: Assemblies not enclosing conditioned space., Clear field thermal bridges, Thermal bridges in uninsulated assemblies, Linear- and point thermal bridges with conductivity less than 3.0 Btu·in/h·ft2 ·°F (0.433 W/(m·K)), Alterations except under section C503.
C402.7.1 5.5.5 | Thermal Bridging Documentation and Mitigation | The following intersections shall be evaluated for thermal bridges and be detailed in construction documents: | ASSEMBLY 1. Structural framing and members. 2. Cladding attachment systems 3. Assembly intersections: a. Roof edge, parapet b. Intermediate floor to wall intersection c. Balcony or overhang to opaque wall intersection d. Balcony in contact with vertical fenestration e. Cladding support - girts or clips f. Wall to vertical fenestration intersection | ASSEMBLY APPLIES-Y/N 1. Structural framing members. Y/N 2. Cladding attachment systems Y/N 3. Assembly intersections: a. Roof edge, parapet Y/N b. Floor to wall intersection Y/N c. Overhang to wall intersection Y/N d. Balcony at vertical fenestration Y/N e. Cladding support- girts or clips Y/N f. Wall to fenestration intersection Y/N | Drawing details on plan A-xx, A-xx ,Narrative and/or Schedule of Inspections on EN-xx and specifications on drawing A-xx | COMPLIES or N/A
C402.7.2 C402.7.2.1 5.5.5.2 | Thermal Bridging of Balconies and Floor decks | Thermal bridges in above-grade walls shall comply with this section or an approved design per Section 102. | Balconies and concrete floor decks shall not penetrate the building thermal envelope except when: 1. An area-weighted U-factor includes a U-factor of 0.8 Btu/h·ft2 ·°F (1.38W/m × K). 2. An approved thermal break device with R-value of not less than R-10 insulation is installed 3. An approved design accounts for all balcony and concrete floor deck thermal bridges. | Balconies and concrete floor decks do not penetrate the building thermal envelope Y/N Balconies and concrete floor decks penetrate the thermal envelope and are mitigated with (describe system 1,2, or 3 to left) | Drawing details on plan A-xx, A-xx ,Narrative and/or Schedule of Inspections on EN-xx and specifications on drawing A-xx | COMPLIES or N/A
C402.7.2 C402.7.2.2 5.5.5.3 | Thermal Bridging of Cladding Attachments | Thermal bridges in above-grade walls shall comply with this section or an approved design per Section 102. | Cladding supports. Linear elements supporting opaque cladding allow the continuous insulation, to pass behind the cladding support element except at the point of attachment except when: 1. Cladding system is supported by an approved design in accordance with Section 102 where the above-grade wall U-factor used for compliance accounts for the cladding support thermal bridge. 2. Anchoring for curtain wall and window wall systems where curtain wall and window wall systems comply with vertical fenestration requirements of Section C402.7.2.4. | Supports or opaque cladding allow the continuous insulation, to pass behind the cladding support element Y/N 1.An approved design (describe system) is used to account for the cladding support thermal bridge. Y/N 2. Anchoring for curtain wall and window wall systems comply with vertical fenestration requirements of Section C402.7.2.4. (describe system) | Drawing details on plan A-xx, A-xx ,Narrative and/or Schedule of Inspections on EN-xx and specifications on drawing A-xx | COMPLIES or N/A
C402.7.2 C402.7.2.3 5.5.5.4 | Thermal Bridging of Structural Beams and Columns | Structural steel and concrete beams and columns that project through the building thermal envelope shall be: | Covered with not less than R-5 insulation on all sides for not less than 2 feet (610 mm) beyond the interior or exterior surface of an insulation component within the building thermal envelope except when: 1. An approved thermal break device is installed in accordance with the manufacturer's instructions or 2. An approved design in accordance with Section102 where the above-grade wall U-factor used to demonstrate compliance accounts for the beam or column thermal bridge. | Beams and Columns are covered with not less than R-5 insulation on all sides for not less than 2 feet(610 mm) beyond the interior or exterior Y/N 1. An approved thermal break device is installed in accordance with the manufacturer's instructions. Y/N 2. An approved design (describe system) is used to account for the beam and column thermal bridge. | Drawing details on plan A-xx, A-xx ,Narrative and/or Schedule of Inspections on EN-xx and specifications on drawing A-xx | COMPLIES or N/A
C402.7.2 C402.7.2.4 C402.7.2.4.1 5.5.5.4 | Thermal Bridging of Vertical Fenestration | Vertical fenestration intersections with above grade walls shall comply with one or more of the following: | 1. Where above-grade walls include continuous insulation, the plane of the exterior glazing layer or non-metal thermal break in the frame shall be positioned within 2 inches (610 mm) of the interior or exterior surface of the continuous insulation. 2. Where above-grade walls do not include continuous insulation, the plane of the exterior glazing layer or non-metal thermal break in the frame shall be positioned within the thickness of the integral or cavity insulation. 3. The surface of the rough opening, not covered by the fenestration frame, shall be insulated with insulation of not less than R-3 material or covered with a wood buck that is not less than 1.5 inches (457 mm) thick except when: 1. An approved design in accordance with Section 102 for the above grade wall U-factor used for compliance accounts for thermal bridges at the intersection with the vertical fenestration | The above-grade walls include continuous insulation and the plane of the exterior glazing layer or non-metal thermal break in the frame is positioned within 2 inches (610 mm) of the interior or exterior surface of the continuous insulation. Y/N 2. The above-grade walls do not include continuous insulation and the plane of the exterior glazing layer or non-metal thermal break in the frame is positioned within the thickness of the integral or cavity insulation. Y/N 3. The surface of the rough opening, not covered by the fenestration frame is insulated to not less than R-3 material or covered with a wood buck that is not less than 1.5 inches thick Y/N Ex 1. An approved design (describe system) is used to account for thermal bridges at the intersection with the vertical fenestration | Drawing details on plan A-xx, A-xx ,Narrative and/or Schedule of Inspections on EN-xx and specifications on drawing A-xx | COMPLIES or N/A
C402.7.2 C402.7.2.4 C402.7.2.4.1 5.5.5.4 | Thermal Bridging of Vertical Fenestration | Vertical fenestration with spandrels shall comply with one of the following: | 1. For the intersection between vertical fenestration and opaque spandrel in a shared framing system, manufacturer's data for the spandrel U-factor shall account for thermal bridges. 2. Use Default values as listed in C303.1.5 | 1. For the intersection between vertical fenestration and opaque spandrel in a shared framing system, manufacturer's data for the spandrel U-factor shall account for thermal bridges. Y/N 2. Default values as listed in C303.1.5 have been proposed and are listed : Spandrel xx - (describe system with U-value) Spandrel xx - (describe system with U-value) Spandrel xx - (describe system with U-value) | Drawing details on plan A-xx, A-xx ,Narrative and/or Schedule of Inspections on EN-xx and specifications on drawing A-xx | COMPLIES or N/A
C402.7.2 C402.7.2.4 C402.7.2.4.1 5.5.5.1.2 | Thermal Bridging of Parapets | Parapets shall comply with one or more of the following as applicable: | 1. Where continuous insulation is installed on the exterior side of the above-grade wall and the roof is insulated with insulation entirely above deck, the continuous insulation shall extend up both sides of the parapet not less than 2 feet (610 mm) above the roof covering or to the top of the parapet, whichever is less. 2. Where continuous insulation is installed on the exterior side of the above-grade wall and the roof insulation is below the roof deck, the continuous insulation shall extend up the exterior side of the parapet to the top surface of the roof assembly. 3. Where the roof is insulated with insulation entirely above deck, the wall cavity insulation shall extend into the parapet up to the exterior face of the roof insulation or insulation shall be installed not less than 2 feet (610 mm) horizontally inward on the underside of the roof deck. 4. Where continuous insulation is not installed on the exterior side of the above grade wall and the roof insulation is below the roof deck, the wall and roof insulation components shall be continuous and adjacent to each other at the roof ceiling-wall intersection. 5. Where a thermal break device with not less than R-10 insulation material aligned with the above-grade wall and roof insulation is installed in accordance with the manufacturer's instructions. | Roof Insulation is (describe roof assembly and include type., thickness, rated R-value and location ) Wall Insulation is (describe wall assembly and include type., thickness, rated R-value and location ) Parapet is insulated by (choose 1-5 to left and describe assembly) | Drawing details on plan A-xx, A-xx ,Narrative and/or Schedule of Inspections on EN-xx and specifications on drawing A-xx | COMPLIES or N/A
Black Text - Compliance Information DO NOT EDIT
Red Text - New Compliance Requirements for 2025 NYCECC
Blue Text - Proposed Values to be input by Applicant

## Com.ECC - HVAC
2025 NYCECC Tabular Analysis Commercial Building - Envelope
Energy Code Scope of Work - Climate Zone 4
Job # | xxxxxxxxx | DOBNOW Job Type: | e.g. NB, Alt-CO, Alteration | DOB NOW Work Type: | e.g. I-1/GC- , P-2/ MS, PL
Filing Scope of Work |  | Enter PW-1 Scope of Work. Provide additional information and detailed description of Energy Code related work included in this Tabular Analysis
Note for ALTERATION job application: For each altered element where ALTERATION-specific exception/allowance is applied, edit the applicable row in the Proposed Design Value to cite the code section and to report the Supporting Documentation location. For examples of ALTERATION-specific exceptions/allowances, refer to 101.2.5 and C503.1
Does the alteration Scope of Work constitute: A Change of Use to the Building or any of the Spaces __________ or A major modification to the HVAC System(s).___________ For all ALTERATION job applications where the proposed scope of alteration work is limited to partial areas of the existing buildings and/or conditions, please provide a detailed description of the Area of Work, Proposed scope of work and itemize the specific altered elements in the tabular format below.
Professional Statement: "To the best of my knowledge, belief and professional judgment, this application is in compliance with the 2025 New York City Energy Conservation Code |  |  |  |  | Chapter C4 or NYC ASHRAE 90.1 "
NYCECC Citation | Provision | Item Description | Code Prescriptive Value (ECC) | Proposed Design Value | Supporting Documentation | Code Compliance
ENVELOPE COMPONENTS
C403.1.1. 6.4.2.1 | Calculation of heating and cooling loads | Design loads associated with heating, ventilating and air conditioning of the building shall be determined in accordance with ANSI/ASHRAE/ACCA Standard 183 or by an approved equivalent computational procedure per Chapter 3. | Heating and cooling loads shall be adjusted to account for load reductions that are achieved where energy recovery systems are utilized in the HVAC system in accordance with the ASHRAE HVAC Systems and Equipment Handbook by an approved equivalent computational procedure.. |  | Notes on plan M-xx, M-xx and compliance statement on drawing EN- xx | COMPLIES or N/A
C403.1.3 6.10 | Electric-resistance space heating. | Dwelling units and sleeping units using electric-resistance space heating shall limit the total installed heating capacity of all electric-resistance space heating to no more than 2.0 kW per unit.. | All other occupiable spaces within the building using electric-resistance space heating shall limit the total installed heating capacity of all electric-resistance space heating to not more than either of the following: 1. 2.5 W per square foot. 2. 5 percent of the total building HVAC system heating cap. unless allowed per exceptions C403.1.3 ( 1-5) or 6.10 | Heating capacity of all electric-resistance space heating is no more than 2.0 kW per unit.. Y/N Heating and cooling loads have been adjusted to allow for exception (number) Describe exception including space type, area, equipment and capacity | Notes on plan M-xx, M-xx and compliance statement on drawing EN- xx | COMPLIES or N/A
C403.2.1. 6.4.3.3.4 | Zone Isolation | Ventilation, either natural or mechanical, shall be provided in accordance with Chapter 4 of the New York City Mechanical Code. | Each isolation area shall be equipped with isolation devices and controls configured to automatically shut off the supply of conditioned air and outdoor air to and exhaust air from the isolation area. Each isolation area shall be controlled independently by a device meeting the requirements of Section C403.4.2.2. Central systems and plants shall be provided with controls and devices that will allow system and equipment operation for any length of time while serving only the smallest isolation area served by the system or plant unless allowed per exceptions C403.2.1 ( 1-3) or 6.4.3.3.4 | HVAC Zones serving over 25,000 square feet (2323 m2) in floor area or that span more than one floor are isolated Y/N Zone Isolation has been adjusted to allow for exception (number) Describe exception including space type, area, equipment and capacity | Notes on plan M-xx, M-xx and compliance statement on drawing EN- xx | COMPLIES or N/A
C403.2.2 6.4.3.4 | Ventilation | HVAC systems serving zones that are over 25,000 square feet (2323 m2) in floor area or that span more than one floor and are designed to operate or be occupied nonsimultaneously shall be divided into isolation areas. | Where mechanical ventilation is provided, the system shall provide the capability to reduce the outdoor air supply to the minimum required by Chapter 4 of the New York City Mechanical Code. | Mechanical ventilation is provided and the system has reduced outdoor air supply to the minimum required . Total Outdoor air shall not exceed (provide both total CFM and Cfm/sq. ft.) | Ventilation Plans &Notes on drawing M-xx, M-xx, Ventilation riser diagrams on M-xx and Schedules on M-xx | COMPLIES or N/A
C403.3 C403.3.1 C403.3.2 | HVAC equipment efficiencies & Performance Requirements | Heating and cooling equipment installed in mechanical systems shall be sized in accordance with Section C403.3.1 and shall be not less efficient in the use of energy than as specified in Section C403.3.2. | C403.3.1 Equipment sizing. The output capacity of heating and cooling equipment shall be not greater than that of the smallest available equipment size that exceeds the loads calculated in accordance with Section C403.1.1. C403.3.2 HVAC equipment performance requirements. Equipment shall meet the minimum efficiency requirements of Tables C403.3.2(1) through C403.3.2(16) when tested and rated in accordance with the applicable test procedure. ... | Heating and cooling equipment installed in mechanical systems has been sized in accordance with Section C403.3.1. Y/N 'Heating and cooling equipment is not less efficient in the use of energy than as specified in Section C403.3.2 Y/N | Notes on plan M-xx, M-xx and compliance statement on drawing EN- xx | COMPLIES or N/A
Table C403.3.2 6.4.1 | MIN. EFFICIENCY REQUIREMENTS | NYCECC Tables in this code are intended to be a restatement of the legally binding provisions found in Title 10 CFR Part 431 included here as a convenience). Lists below are not comprehensive. All efficiencies are shown with electric resistance heating. For equipment or capacities not listed below , refer to Table C403.3.2. Where Code required ASHRAE values are applied, refer to Section 6.4.1 and Table 6.8.1 and indicate both code require and proposed efficiencies.
Table C403.3.2(1) | ELECTRICALLY OPERATED UNITARY AIR CONDITIONERS AND CONDENSING UNITS | Heating and cooling equipment installed in mechanical systems shall be sized in accordance with Section C403.3.1 and shall be not less efficient in the use of energy than as specified in Section C403.3.2. | EQUIPMENT TYPE SIZE (Btu/H) MIN. EFF. Air conditioners, air cooled < 65,000 13.4 SEER2 Small duct, high vel.,air cooled ≤ 65,000 13.0 SEER2 Air conditioners, air cooled ≥ 65< 135 14.8 IEER Air conditioners, air cooled ≥ 135 <240 14.2 IEER Air conditioners, water cooled < 65.,000 12.3 IEER Air conditioners, water cooled ≥ 65< 135 13.9 IEER Air conditioners, water cooled ≥ 135 <240 13.9 IEER Condensing units, air cooled ≥ 135,000 11.8 IEER Condensing units water& evap. ≥ 135,000 14.0 IEER | EQUIPMENT TYPE SIZE MIN. EFF. Air conditioners, air cooled < 65,000 1x.x SEER2 Small duct, high vel.,air cooled ≤ 65,000 1x.x SEER2 Air conditioners, air cooled ≥ 65< 135 1x.x IEER Air conditioners, air cooled ≥ 135 <240 1x.x IEER Air conditioners, water cooled < 65.,000 1x.x IEER Air conditioners, water cooled ≥ 65< 135 1x.x IEER Air conditioners, water cooled ≥ 135 <240 1x.x IEER Condensing units, air cooled ≥ 135,000 1x.x IEER Condensing units water& evap. ≥ 135,000 1x.x IEER | Plans on M-xx, M-xx , Mechanical Schedule on M-xx and specifications on drawing M-xx | COMPLIES or N/A
Table C403.3.2(2) | ELECTRICALLY OPERATED AIR-COOLED UNITARY HEAT PUMPS | Heating and cooling equipment installed in mechanical systems shall be sized in accordance with Section C403.3.1 and shall be not less efficient in the use of energy than as specified in Section C403.3.2. | EQUIPMENT TYPE SIZE (Btu/H) MIN. EFF. Heat Pump, air cooled 3ph. < 65,000 14.3 SEER2 Small duct, high vel.,air 3ph ≤ 65,000 14.0 SEER2 Heat Pumps, air cooled ≥ 65< 135 14.1 IEER Heat Pumps, air cooled ≥ 135 <240 13.5 IEER Heat Pump, split 3ph, air/ htg < 65.,000 7.5 HSPF2 Small duct, high vel.,air/ htg ≤ 65,000 6.9 HSPF2 Heat Pumps, air/heating ≥ 65< 135 3.4 COP 47 Heat Pump, air/heating ≥ 135 <240 3.3 COP 47 | EQUIPMENT TYPE SIZE MIN. EFF. Heat Pump, air cooled 3ph. < 65,000 xx SEER2 Small duct, high vel.,air 3ph ≤ 65,000 xx SEER2 Heat Pumps, air cooled ≥ 65< 135 xx IEER Heat Pumps, air cooled ≥ 135 <240 xx IEER Heat Pump, split 3ph, air/ heating < 65.,000 xx HSPF2 Small duct, high vel.,air/ heating ≤ 65,000 xx HSPF2 Heat Pumps, air/heating ≥ 65< 135 xx COP 47 Heat Pump, air/heating ≥ 135 <240 xx COP 47 | Plans on M-xx, M-xx , Mechanical Schedule on M-xx and specifications on drawing M-xx | COMPLIES or N/A
Table C403.3.2(4) | ELECTRICALLY OPERATED PTACs, PTHPs, SPVACs, SPVHPs, ROOM AC & ACHP | Heating and cooling equipment installed in mechanical systems shall be sized in accordance with Section C403.3.1 and shall be not less efficient in the use of energy than as specified in Section C403.3.2. | EQUIPMENT SIZE (Btu/H) MIN. EFF. PTAC/PTHP, cooling < 7,000 11.9 EER PTAC/PTHP, clg. > 7<15 14 –(0.300 × Cap/1,000) EER PTAC/PTHP, clg. >15,000 9.5 EER PTHP, heating < 7,000 3.30 COP PTHP, heating > 7<15 3.7 –(0.052 × Cap/1,000) COP PTHP, heating >15,000 2.90 COP SPVAC/SPVHP, clg. ≤ 65,000 11.0 EER SPVAC/SPVHP, clg. ≥ 65 <135 10.0 EER SPVAC/SPVHP, clg ≥ 135 <240 10.0 EER SPVAC/SPVHP, htg. ≤ 65,000 3.30 COP SPVAC/SPVHP, htg. ≥ 65 <135 3.00 COP SPVAC/SPVHP, htg ≥ 135 <240 3.00 COP | EQUIPMENT SIZE (Btu/H) MIN. EFF. PTAC/PTHP, cooling < 7,000 xx EER PTAC/PTHP, clg. > 7<15 14 –(0.300 × Cap/1,000) EER PTAC/PTHP, clg. >15,000 xx EER PTHP, heating < 7,000 xx COP PTHP, heating > 7<15 3.7 –(0.052 × Cap/1,000) COP PTHP, heating >15,000 xx COP SPVAC/SPVHP, clg. ≤ 65,000 1x.x EER SPVAC/SPVHP, clg. ≥ 65 <135 1x.x EER SPVAC/SPVHP, clg ≥ 135 <240 1x.x EER SPVAC/SPVHP, htg. ≤ 65,000 x. xx COP SPVAC/SPVHP, htg. ≥ 65 <135 x.xx COP SPVAC/SPVHP, htg ≥ 135 <240 x.xx COP | Plans on M-xx, M-xx , Mechanical Schedule on M-xx and specifications on drawing M-xx | COMPLIES or N/A
Table C403.3.2(9) | ELECTRICALLY OPERATED VARIABLE REFRIGERANT FLOW AND APPLIED HEAT PUMPS - AIR COOLED | Heating and cooling equipment installed in mechanical systems shall be sized in accordance with Section C403.3.1 and shall be not less efficient in the use of energy than as specified in Section C403.3.2. | EQUIPMENT TYPE SIZE(Btu/H) MIN. EFF. VRF , air cooled, 3ph < 65,000 13.4 SEER2 VRF, air cooled, multi ≥ 65< 135 14.6 IEER VRF, air cool, ht. recvy. ≥ 65< 135 14.4 IEER VRF, air cooled, multi >135 <240 14.4 IEER VRF, air cool, ht. recvy. >135 < 240 13.7 IEER VRF, air cooled, multi ≥ 240 12.7 IEER VRF, air cool, ht. recvy. ≥ 240 12.5 IEER VRF, air cool, heating ≤ 65,000 7.5 HSPF2 VRF, air cool, heating ≥ 65 <135 3.30 COP 47 VRF, air cool, heating ≥ 135, 000 3.20 COP 47 | EQUIPMENT TYPE SIZE(Btu/H) MIN. EFF. VRF , air cooled, 3ph < 65,000 xx SEER2 VRF, air cooled, multi ≥ 65< 135 xx IEER VRF, air cool, ht. recvy. ≥ 65< 135 xx IEER VRF, air cooled, multi >135 <240 xx IEER VRF, air cool, ht. recvy. >135 < 240 xx IEER VRF, air cooled, multi ≥ 240 xx IEER VRF, air cool, ht. recvy. ≥ 240 xx IEER VRF, air cool, heating ≤ 65,000 xx HSPF2 VRF, air cool, heating ≥ 65 <135 xx COP 47 VRF, air cool, heating ≥ 135, 000 xx COP 47 | Plans on M-xx, M-xx , Mechanical Schedule on M-xx and specifications on drawing M-xx | COMPLIES or N/A
Table C403.3.2(9) | ELECTRICALLY OPERATED VARIABLE REFRIGERANT FLOW AND APPLIED HEAT PUMPS - WATER COOLED | Heating and cooling equipment installed in mechanical systems shall be sized in accordance with Section C403.3.1 and shall be not less efficient in the use of energy than as specified in Section C403.3.2. | EQUIPMENT TYPE SIZE(Btu/H) MIN. EFF. VRF ,water cooled, multi < 135,000 16.0 IEER VRF ,water cooled, ht.recvy < 135,000 15.8 IEER VRF, water cooled, multi >135 <240 14.0 IEER VRF, water cool, ht. recvy. >135 < 240 13.8 IEER VRF, water cooled, multi ≥ 240 12.0 IEER VRF, water cool, ht. recvy. ≥ 240 11.8 IEER VRF, water source, heating ≤ 65,000 4.3 COP 68 VRF, water source, heating ≥ 65 <135 4.3 COP 68 VRF, water source, heating >135 < 240 4.0 COP 68 VRF, water source, heating > 240,000 3.9 COP 68 | EQUIPMENT TYPE SIZE(Btu/H) MIN. EFF. VRF ,water cooled, multi < 135,000 xx.x IEER VRF ,water cooled, ht.recvy < 135,000 xx.x IEER VRF, water cooled, multi >135 <240 xx.x IEER VRF, water cool, ht. recvy. >135 < 240 xx.x IEER VRF, water cooled, multi ≥ 240 xx.x IEER VRF, water cool, ht. recvy. ≥ 240 xx.x IEER VRF, water source, heating ≤ 65,000 x.x COP 68 VRF, water source, heating ≥ 65 <135 x.x COP 68 VRF, water source, heating >135 < 240 x.x COP 68 VRF, water source, heating > 240,000 x.x COP 68 | Plans on M-xx, M-xx , Mechanical Schedule on M-xx and specifications on drawing M-xx | COMPLIES or N/A
Table C403.3.2(12) | ELECTRICALLY OPERATED DX-DOAS UNITS, SINGLE PACKAGE & REMOTE CONDENSER WITH ENERGY RECOVERY | Heating and cooling equipment installed in mechanical systems shall be sized in accordance with Section C403.3.1 and shall be not less efficient in the use of energy than as specified in Section C403.3.2. | EQUIPMENT TYPE MIN. EFF Air cooled DX (dehumid mode) 5.0 ISMRE2 Air-source heat pumps (dehumid mode) 5.0 ISMRE2 Water cooled (dehumid) Cooling tower 5.1 ISMRE2 Air-source heat pump (heating mode) 3.2 ISCOP2 Water-source heat pump (dehumid) Water 4.6 ISMRE2 Water-source heat pump (heating )Water 4.04 ISCOP2 | EQUIPMENT TYPE MIN. EFF Air cooled DX (dehumid mode) x.x ISMRE2 Air-source heat pumps (dehumid mode) x.x ISMRE2 Water cooled (dehumid) Cooling tower x.xI SMRE2 Air-source heat pump (heating mode) x.x ISCOP2 Water-source heat pump (dehumid) Water x.x ISMRE2 Water-source heat pump (heating )Water x.x ISCOP2 | Plans on M-xx, M-xx , Mechanical Schedule on M-xx and specifications on drawing M-xx | COMPLIES or N/A
Table C403.3.2(14) | ELECTRICALLY OPERATED WATER-SOURCE HEAT PUMPS | Heating and cooling equipment installed in mechanical systems shall be sized in accordance with Section C403.3.1 and shall be not less efficient in the use of energy than as specified in Section C403.3.2. | EQUIPMENT TYPE SIZE(Btu/H) MIN. EFF. Water-to-air, water loop (clg) < 17,000 12.2 EER @ 86 Water-to-air, water loop (clg)≥ 17 < 65 13.0 EER @86 Water-to-air, water loop (clg)≥ 65< 135 13.0 EER @ 86 Water-to-water, water lp (clg) < 135,000 10.6 EER @86 Water-to-water, water lp (htg) < 135,000 4.3 COPH @68 | EQUIPMENT TYPE SIZE(Btu/H) MIN. EFF. Water-to-air, water loop (clg) < 17,000 x.x EER @ 86 Water-to-air, water loop (clg)≥ 17 < 65 x.x EER @86 Water-to-air, water loop (clg)≥ 65< 135 x.x EER @ 86 Water-to-water, water lp (clg) < 135,000 x.x EER @86 Water-to-water, water lp (htg) < 135,000 x.x COP @68 | Plans on M-xx, M-xx , Mechanical Schedule on M-xx and specifications on drawing M-xx | COMPLIES or N/A
C403.4 6.4.3 | HEATING & COOLING SYSTEMS CONTROLS | Heating and cooling system shall be provided with controls in accordance with Sections C403.4.1 through C403.4.8 or ASHRAE 6.4.3
C403.4.1 6.4.3.1 | Thermostatic Control | Provide a Thermostat, and humidistat as applicable, for each heating and cooling zone | The supply of heating and cooling energy to each zone shall be controlled by individual thermostatic controls capable of responding to temperature within the zone. Where humidification or dehumidification or both is provided, not fewer than one humidity control device shall be provided for each humidity control system, unless allowed per exception C403.4.1 (1 &2) or 6.4.3.1 | Each zone is controlled by individual thermostatic controls capable of responding to temperature within the zone Y/N One humidity control device is provided for each humidity control system, where applicable. Y/N | Thermostats shown on drawing M-xx, M-xx, and Schedules or specifications on M-xx indicate setpoints | COMPLIES or N/A
C403.4.1.1 6.4.3.5 | Heat Pump Supplementary Heat | Heat pumps having supplementary electric resistance, fuel gas, or liquid fuel heating systems shall have controls that limit supplemental heat operation to only those times when one of the following applies: | 1. The vapor compression cycle cannot provide necessary heating energy to satisfy the thermostat setting where controls are installed such that supplementary heat shall operate only when the outdoor air temperature is less than 17°F and supplemental heat capacity does not exceed 25 percent of the total design load. 2. The heat pump is operating in defrost mode. 3. The vapor compression cycle malfunctions. 4. The thermostat malfunctions. | 1. Supplementary heat provided by ( describe system) is installed and shall operate only when the outdoor air temperature is less than 17°F and the vapor compression cycle cannot provide necessary heating energy to satisfy the thermostat setting. Additional controls have been installed to allow operation only when: 2. The heat pump is operating in defrost mode. Y/N 3. The vapor compression cycle malfunctions. Y/N 4. The thermostat malfunctions. Y/N | Supplementary Systema and Controls shown on drawing M-xx, M-xx, and Schedules or specifications on M-xx indicate setpoints | COMPLIES or N/A
C403.4.1.2 6.4.3.1.2 | Deadband Control | Provide Deadband Controls for Thermostats | Where used to control both heating and cooling, zone thermostatic controls shall: 1. Have separate setpoints for heating and cooling, each individually adjustable. 2. Be capable of and initially configured to provide a temperature range or deadband between the two setpoints of not less than 5°F (3°C) within which the supply of heating and cooling energy to the zone is shut off or reduced to a minimum. 3. Have a minimum deadband of not less than 1°F (0.56°C) when setpoints are adjusted. | 1. 'Each zone has separate setpoints for heating and cooling, each individually adjustable. Y/N 2. Each thermostat is capable of being configured to provide a temperature range or deadband between the two setpoints of not less than 5°F (3°C) within which the supply of heating and cooling energy to the zone is shut off or reduced to a minimum. Y/N 3. Each thermostat is capable of having a minimum deadband of not less than 1°F (0.56°C) when setpoints are adjusted. Y/N | Schedules or specifications on M-xx indicate setpoints | COMPLIES or N/A
C403.4.1.6 | Hot water boiler outdoor temperature setback control | Provide Setback Controls for Boilers | Hot water boilers that supply heat to the building through one- or two-pipe heating systems shall have an outdoor setback control that lowers the boiler water temperature based on the outdoor temperature | An outdoor setback control lowers the boiler water temperature based on the outdoor temperature. Y/N | Schedules or specifications on M-xx indicate setpoints | COMPLIES or N/A
C403.4.2 C403.4.2.1 C403.4.2.2 C403.4.2.3 6.4.3.3 | Off Hours Controls | Each zone shall be provided with thermostatic setback controls that are controlled by either an automatic time clock or programmed control system. | 1 Thermostatic setback controls shall be configured to set back or temporarily operate the system to maintain zone temperatures down to 55°F (13°C) or up to 85°F (29°C). 2.Automatic time clock or programmable controls shall be capable of starting and stopping the system for seven different daily schedules per week. 3.Optimum start and stop controls shall be provided for each heating and cooling system with direct control of individual zones | Thermostatic setback controls shall be configured for temperatures down to 55°F (13°C) or up to 85°F (29°C) Y/N Time clock or controls are programmed to start and stop the system for seven schedules per week. Y/N Optimum start and stop controls are provided for each heating and cooling system with direct control of individual zones. Y/N | Schedules or specifications on M-xx indicate setpoints | COMPLIES or N/A
C403.4.6 | Demand Responsive Controls | Electric heating and cooling systems shall be provided with demand responsive controls capable of executing the following actions in response to a demand response signal: | Automatically increase the cooling set point or decrease the heating setpoint by the following values: 1°F (0.5°C), 2°F (1°C), 3°F (1.5°C), and 4°F (2°C) while maintaining the minimum room temperature requirements of the New York City Building Code. The demand responsive controls shall comply with either Section C403.4.6.1 or C403.4.6.2 unless allowed per exceptions C403.4.6 ( 1-5) | Demand Responsive Controls will increase the cooling set point or decrease the heating setpoint by the following values: 1°F (0.5°C), 2°F (1°C), 3°F (1.5°C), and 4°F (2°C) . Demand response is not proposed for ( describe exceptions or alternative control strategy) | Schedules or specifications on M-xx indicate setpoints | COMPLIES or N/A
C403.4.7 6.5.10 | Openings to Outdoors | All doors from a conditioned space to the outdoors and all other operable openings from a conditioned space to the outdoors that are larger than 40 sq. ft.(3.7 m2) when fully open shall have automatic controls interlocked with the heating and cooling system.. | Controls shall do the following within 5 minutes of opening: 1. Disable mechanical heating to the zone or reset the space heating temperature setpoint to 55°F (12.5°C) or less. 2. Disable mechanical cooling to the zone or reset the space cooling temperature setpoint to 90°F (32°C) or more. Mechanical cooling can remain enabled if the outdoor air temperature is below the space temperature. Controls required unless allowed per exceptions C403.4.7( 1-9) | Door Opening Controls will: Disable mechanical heating. Y/N Reset the space heating setpoint to 55°F (12.5°C) Y/N Disable mechanical cooling. Y/N Reset the space cooling setpoint to 90°F (32°C) Y/N Door controls are not proposed for ( describe exceptions or alternative control strategy) | Schedules or specifications on M-xx indicate setpoints | COMPLIES or N/A
C403.5 6.5.1 | Economizers | Economizers shall comply with sections C403.5.1 through C403.5.5 related to capacity, controls, high limit shutoff, automatic dampers and fault detection and diagnostics. | Economizers shall be provide for all systems per C403.5 or 6.5.1 unless allowed by exceptions C403.5 (1-6) or 6.5.1. All Economizers shall have Integrated economizer control per C405.5.1. Air Economizers shall meet the requirements of C403.5.3 or 6.5.1.1. Water Economizers shall meet the requirements of C403.5.4 or 6.5.1.2 Fault detection and diagnostics shall meet the requirements of C403.5.3 or 6.4.3.12 | Economizers are be provide for all systems unless allowed by exceptions C403.5 (1-6) or 6.5.1. Y/N Economizers have Integrated economizer control. Y/N Air Economizers are installed in describe location and system capacity . Water Economizers are installed in describe location and system capacity Fault detection and diagnostics are proposed Y/N | Plans on M-xx, M-xx , Mechanical Schedule on M-xx and specifications on drawing M-xx | COMPLIES or N/A
C403.6 6.4.3.1 | Mechanical systems serving multiple zones: VAV & multi-zone systems | Each zone shall be provided with thermostatic setback controls that are controlled by either an automatic time clock or programmed control system, | VAV & multi-zone systems shall meet the requirements of C403.6.1through C403.6.4 unless allowed by exceptions C403.6.1 (1-2). Multi-zone supply air temperature reset shall meet the requirements of C403.6.5 unless allowed by exceptions C403.6.5 (1-2). 'VAV & multi-zone systems controls strategy shall meet the requirements of C403.6.6 through C403.6.9 | VAV & multi-zone systems proposed. Y/N Supply air temperature reset proposed . Y/N Systems controls strategy proposed Y/N | Plans on M-xx, M-xx , Mechanical Schedule on M-xx and specifications on drawing M-xx | COMPLIES or N/A
C403.7 6.4.3.4 | VENTILATION & EXHAUST SYSTEMS | In addition to requirements of Section C403 applicable to the provision of ventilation air or the exhaust of air, ventilation and exhaust systems shall be in accordance with Sections C403.7.1 through C403.7.9
C403.7.1 6.4.3.8 | Demand control ventilation (DCV) | Demand control ventilation (DCV) shall be provided for the following: | 1. Spaces with ventilation provided by single-zone systems where an air-side economizer is provided per C403.5. 2. Spaces larger than 500 square feet (46.5 m2 ) that have a design occupant load of 15 people or greater per 1,000 sq. ft. (93 m2 ) of floor area, as established in the New York City Mechanical Code, and are served by systems with one or more of the following: 2.1 An air-side economizer 2.2 Automatic control of the outdoor air damper. 2.3. A design outdoor airflow greater than 3,000 cfm (1416 L/s), unless allowed per exception C403.7.1 (1 -6) or 6.4.3.8 | Ventilated spaces proposed to have an air-side economizer per C403.5. or 6.4.3.8 ( describe spaces) Project has spaces larger than 500 square feet (46.5 m2 ) that have a design occupant load of 15 people or greater per 1,000 sq. ft. (93 m2 ) of floor area, and are served by 2.1 An air-side economizer Y/N 2.2 Automatic control of the outdoor air damper. Y/N 2.3. A design outdoor airflow greater than 3,000 cfm Y/N Controls are not proposed for ( describe exceptions or alternative control strategy) | DCV shown on drawing M-xx, M-xx, and Schedules or specifications on M-xx indicate setpoints | COMPLIES or N/A
C403.7.2 6.4.3.4.5 | Parking garage Ventilation controls | Ventilation systems employed in enclosed parking garages shall comply with New York City Mechanical Code and the following: | 1. Separate ventilation systems and control systems shall be provided for each parking garage section. 2. Control systems for each parking garage section shall be capable of and configured to reduce fan airflow to not less than 0.05 cfm/sq. ft of the floor area served and not more than 20 percent of the design capacity. 3. The ventilation system for each parking garage section shall have controls and devices that result in fan motor demand of not more than 30 percent of design wattage at 50 percent of the design airflow. | 1. Separate ventilation systems and control systems are provided for each parking garage section. Y/N 2. Control systems for each parking garage section are configure to reduce fan airflow to not less than 0.05 cfm/sq. ft of the floor area served and not more than 20 percent of the design capacity. Y/N 3. The ventilation system for each parking garage section will have controls and devices that result in fan motor demand of not more than 30 percent of design wattage at 50 percent of the design airflow. Y/N | Ventilation & Controls shown on drawing M-xx, M-xx, and Schedules or specifications on M-xx indicate setpoints | COMPLIES or N/A
C403.7.3 | Ventilation air heating control | HVAC units for multiple zones | Units that provide ventilation air to multiple zones and operate in conjunction with zone heating and cooling systems shall not use heating or heat recovery to warm supply air to a temperature greater than 60°F (16°C) when representative building loads or outdoor air temperatures indicate that the majority of zones require cooling, unless allowed per exception C403.7.3 | Zone heating and cooling systems will not use heating or heat recovery to warm supply air to a temperature greater than 60°F (16°C) Y/N | Ventilation & Controls shown on drawing M-xx, M-xx, and Schedules or specifications on M-xx indicate setpoints | COMPLIES or N/A
C403.7.4.1 6.5.6.1.1 | Energy Recovery Systems Non-Transient Dwelling Units | Energy recovery ventilation systems shall be provided as specified in Section C403.7.4.1 or 6.5.6.1.1, as applicable. | Each unit shall be provided with outdoor air energy recovery ventilation complying with not less than one of the following: 1. The system shall have an enthalpy recovery ratio of not less than 50 percent at cooling design condition and not less than 60 percent at heating design condition. 2. The system shall have a sensible recovery efficiency (SRE) that is not less than 65 percent at 32°F (0°C). SRE and NMT shall be determined from a listed value. | 1. Proposed systems will have an enthalpy recovery ratio of not less than 50 percent at cooling design condition and not less than 60 percent at heating design condition. Y/N 2. Proposed systems will have a sensible recovery efficiency (SRE) that is not less than 65 percent at 32°F (0°C). SRE and NMT shall be determined from a listed value. Y/N | Thermostats shown on drawing M-xx, M-xx, and Schedules or specifications on M-xx indicate setpoints | COMPLIES or N/A
C403.7.4.2 Tables C403.7.4.2(1)Tables C403.7.4.2(2) 6.5.6.1.2 | Energy Recovery Systems for other than Non-Transient Dwelling Units | Energy recovery ventilation systems shall be provided as specified in Section C403.7.4.2 0r 6.5.6.1.2, as applicable. | Where the supply airflow rate of a fan system serving a space other than a nontransient dwelling unit exceeds the values specified in Tables C403.7.4.2(1) and C403.7.4.2(2), the system shall include an energy recovery system enthalpy recovery ratio of not less than 50 percent, at design conditions. Where an air economizer is required, the energy recovery system shall include a bypass or controls to permit operation of the economizer as required by Section C403.5. or 6.5.6.1.2.2. | The supply airflow rate of the ( describe) fan system serving describe space is ( xx cfm) and exceeds the values specified in Tables C403.7.4.2(1) and C403.7.4.2(2) or Tables 6.5.6.1.2-1 and 6.5.6.1.2-2. An energy recovery system enthalpy recovery ratio of not less than 50 percent, at design conditions is proposed. An air economizer is/ is not required, and will include a bypass or controls to permit operation of the economizer as required by Section C403.5 or 6.5.6.1.2.2. | Energy recovery system Plans on M-xx, M-xx , Mechanical Schedule on M-xx and specifications on drawing M-xx | COMPLIES or N/A
C403.7.5 Table C403.7.5 6.5.7.2 | Kitchen exhaust systems | Kitchen exhaust systems & replacement air | Replacement air introduced directly into the exhaust hood cavity shall not be greater than 10 percent of the hood exhaust airflow rate. Conditioned supply air delivered to any space shall not exceed the greater of the following: 1. The ventilation rate required to meet the space heating or cooling load. 2. The hood exhaust flow minus the available transfer air from adjacent space where available transfer air is considered to be that portion of outdoor ventilation air not required to satisfy other exhaust needs, and not required to maintain pressurization of adjacent spaces. Provide as listed unless allowed per exception C403.7.5 (1&2) | Maximum Net exhaust rate proposed per Table 403.7.5 will be (describe hood type, equipment duty and cfm/lin. Ft.) Replacement air will be provided by: (describe per 1 or 2) at supply rate) | Kitchn exhaust rates and Controls shown on drawing M-xx, M-xx, and Schedules or specifications on M-xx | COMPLIES or N/A
C403.7.6 6.4.3.3.5 | Automatic control of HVAC systems serving guestrooms. | In Group R-1 buildings containing more than 50 guestrooms, each guestroom shall be provided with controls complying with Sections C403.7.6.1 and C403.7.6.2. | 1. When the guestroom is rented but unoccupied, the controls shall automatically raise the cooling setpoint and lower the heating setpoint by not less than 4°F (2°C) from the occupant setpoint within 30 minutes after the occupants have left the guestroom. 2. When the guestroom is unrented and unoccupied, raise the cooling setpoint to not lower than 80°F (27°C) and lower the heating setpoint to not higher than 60°F (16°C). 3. When the guestroom is occupied, HVAC setpoints shall return to their occupied setpoints once occupancy is sensed. | 1. When the guestroom is rented but unoccupied, the cooling setpoint with be raised and the heating setpoint will be lowered by not less than 4°F (2°C) after the occupants have left the guestroom. Y/N 2. When the guestroom is unrented & unoccupied, the cooling setpoint will be not lower than 80°F (27°C) and the heating setpoint will be not higher than 60°F (16°C). Y/N 3. When the guestroom is occupied, HVAC setpoints shall return to their occupied setpoints once occupancy is sensed. Y/N | Thermostats shown on drawing M-xx, M-xx, and Schedules or specifications on M-xx indicate setpoints | COMPLIES or N/A
C403.7.7 6.4.3.4.1 6.4.3.4.2 6.4.3.4.3 | Shutoff dampers | Outdoor air intake and exhaust openings and stairway and shaft vents shall be provided with Class I motorized dampers, where applicable. | The dampers shall have an air leakage rate not greater than 4 cfm/ft2 (20.3 L/s × m2) of damper surface area at 1.0 inch water gauge (249 Pa) and shall be labeled by an approved agency when tested in accordance with AMCA 500D for such purpose. Outdoor air intake and exhaust dampers shall be installed with automatic controls configured to close... unless allowed per exception C403.7.7 (1-3) | Dampers have an air leakage rate not greater than 4 cfm/ft2 (20.3 L/s × m2) of damper surface area at 1.0 inch water gauge (249 Pa) . Y/N Outdoor air intake and exhaust dampers are installed with automatic controls configured to close... Y/N Dampers are provided unless allowed per exception C403.7.7 (describe) Y/N | Dampers shown on drawing M-xx, M-xx, and Schedules or specifications on M-xx indicate type and operation | COMPLIES or N/A
C403.7.8 6.4.3.3.5.1 | Occupied standby controls | Controls per C403.7.8.1 for: 1. Lecture and training rooms. 2. Conference/meeting/ rooms. 3. Lounges/breakrooms. 4. Enclosed offices. 5. Open-plan office areas. 6. Corridors. Controls per 6.4.3.3.5 for Hotel Guest Rooms | C403.7.8.1 Within 5 minute of all spaces in that zone entering occupied-standby, the zone control shall operate as follows: 1. The active heating setpoint set back by not less than 1°F 2. The active cooling setpoint set up by not less than 1°F 3. All airflow supplied to the zone shall be shut off whenever temperature is between active heating and cooling setpoints. 4. Multiple-zone systems shall comply with C403.7.8.1.1. . Automatic Control shall comply with ASHRAE 6.4.3.3.5 | 1. Active heating setpoint setback by not less than 1°F Y/N 2. Active cooling setpoint set up by not less than 1°F Y/N 3. All airflow supplied to the zone shall be shut off whenever the temperature is between active heating and cooling setpoints. Y/N 4. Multiple-zone systems shall comply with C403.7.8.1.1. Y/N . Automatic Control shall comply with ASHRAE 6.4.3.3.5 Y/N | Setpoints indicated on drawing M-xx, M-xx, and Schedules or specifications on M-xx indicate setpoints | COMPLIES or N/A
C403.8 C403.9 6.4.3.4.4 | Fan & Fan Controls | Fans in HVAC systems shall comply with Sections C403.8.1 through C403.8.6.1. Air flow Fans shall comply with C403.9 | Allowable Fan Power shall meet requirements of C403.8.1 Motor nameplate Hp shall meet requirements of C403.8.2 Fan Efficiency shall meet requirements of C403.8.3 Fractional Hp Motors shall meet requirements of C403.8.4 Ventilation & Air flow Fans shall meet requirements of C403.8.5 through C403.9 | Allowable Fan Power = ( per table 403.8.1(1)) Motor nameplate Hp = ( per C403.8.2) Fan Efficiency = ( per C403.8.3 ) Fractional Hp Motors = ( per C403.8.4) Ventilation & Air flow Fans are ( describe per C403.8.5 through C403.9 ) | Fans & Motors shown on drawing M-xx, M-xx, and Schedules or specifications on M-xx indicate type and operation | COMPLIES or N/A
C403.10 Table C403.3.2(6) 6.4.1.6 | High-capacity space-heating gas boiler systems | Boiler systems for space heating with system input capacities of not less than 1,000,000 Btu/h (293 kW) and not greater than 10,000,000 Btu/h | C403.10.1 Gas hot water boilers shall have a thermal efficiency (Et) of not less than 90 percent. C403.10.2 1. Coils and other heat exchangers shall be selected so that at design conditions the hot water return temperature entering the boilers is 120°F (49°C) or less. 2. Under all operating conditions, the water temperature entering the boiler is not greater than 120°F (49°C) | 1. Gas hot water boilers have a Capacity of xxxxxxxxx Btu/H and a thermal efficiency (Et) of not less than 90 percent. 2. Coils, and other heat exchangers, are connected to (describe system) and have a hot water return temperature entering the boilers at xxxx °F ( xxx °C) or less. Under operating conditions, the water temperature entering the boiler is not greater than xxxx °F ( xxx °C) | Gas Boilers shown on drawing M-xx, M-xx, and Schedules or specifications on M-xx indicate type and operation | COMPLIES or N/A
C403.11 6.5.5 | Heat rejection equipment | Heat rejection equipment, including air-cooled condensers, dry coolers, open-circuit cooling towers, closed-circuit cooling towers and evaporative condensers, shall comply with this section. | Fan Speed Control shall meet requirements of C403.11.1 Multi-cell equipment shall meet requirements of C403.11.2 Centrifugal fans shall meet requirements of C403.11.3 Flow Turndown shall meet requirements of C403.11.4 SW heat recovery shall meet requirements of C403.11.5 Heat recovery for healthcare space conditioning. shall meet requirements of C403.11.6 | Fan Speeds are automatically modulated per C403.11.1 Y/N Multi-cell units have speed controls per C403.11.2 Y/N Centrifugal fans meet efficiency limits per C403.11.3 Y/N Flow Turndown meets requirements of C403.11.4 Y/N SW heat recovery meet requirements of C403.11.5 Y/N Heat recovery for healthcare space conditioning meets requirements of Table C403.3.2(15) Y/N | Heat rejection equipment shown on drawing M-xx, M-xx, and Schedules or specifications on M-xx indicate type and operation | COMPLIES or N/A
C403.13 6.4.4.1 | Construction of HVAC system elements - Ducts & Plenums | Ducts, plenums and other elements that are part of an HVAC system shall be constructed and insulated per SectionsC403.13.1 through C403.13.2 | C403.13.1 Supply and return air ducts and plenums shall be insulated with not less than R-6 insulation where located in unconditioned spaces and where located outside the building with not less than R-8 insulation. C403.13.2 In Low-pressure duct systems, longitudinal and transverse joints, seams and connections of supply and return ducts operating at a static pressure less than or equal to 2 inches water gauge (w.g.) (498 Pa) shall be securely fastened and sealed with welds, gaskets, mastics (adhesives), mastic-plus-embedded-fabric systems or tapes C403.13.2.2 In medium-pressure duct systems. Ducts and plenums designed to operate at a static pressure greater than 2 inches water gauge (498 Pa) but less than 3 inches w.g.(747 Pa) shall be insulated & sealed . | 13.1 Supply and return air ducts and plenums located in unconditioned spaces are insulated with not less than R-xx. 13.11 Supply and return air ducts and plenums located outside the building are insulated with not less than R-xx 13.2 Low-pressure duct systems, longitudinal and transverse joints, seams and connections of supply and return ducts are securely fastened and sealed with (welds, gaskets, mastics (adhesives), mastic-plus-embedded-fabric systems or tape) C403.13.2.2 Medium-pressure ducts and plenums are insulated & sealed ( describe) | Setpoints indicated on drawing M-xx, M-xx, and Schedules or specifications on M-xx indicate setpoints | COMPLIES or N/A
C403.13.3 Table C403.13.3(1) Table C403.13.3(2).6.4.4.1 | Construction of HVAC system elements- Piping | Piping and other elements that are part of an HVAC system shall be constructed and insulated per Section C403.13.3 | C403.13.3 Piping serving as part of a heating or cooling system shall be thermally insulated in accordance with Table C403.13.3(1) or C403.13.3(2). C403.13.3.1 Piping insulation exposed to the weather shall be protected from physical damage, including that caused by sunlight, moisture, equipment maintenance and wind. The protection shall provide shielding from solar radiation that can cause degradation of the material. | 13.3 (HVAC system type) has an operating temperature range of xx - xx F and is insulated with not less than R-xx. '13.3 (HVAC system type) has an operating temperature range of xx - xx F and is insulated with not less than R-xx. '13.3.1 (HVAC system type) has piping exposed to weather and is protected with xx and insulated with not less than R-xx. | Piping details on drawing M-xx, M-xx, and Schedules or specifications on M-xx indicate setpoints | COMPLIES or N/A
C403.14 6.4.3.7 | Mechanical systems located outside of the building thermal envelope. | Mechanical systems providing heat outside of the building thermal envelope of a building shall comply with Sections C403.14.1 through C403.14.4 | 14.1 Heating outside a building. Systems installed to provide heat outside a building shall be radiant systems. 14.2. Snow- and ice-melting systems shall include automatic controls configured to shut off the system when pavement temperature is above 50°F (10°C) with no precipitation. 14.3 Roof and gutter deicing systems shall include automatic controls configured to shut off the system when the outdoor temperature is above 40°F (4°C) 14.4 Freeze protection systems shall include automatic controls configured to shut off the systems when outdoor air temperatures are above 40°F (4°C) | 1 Heating outside the building is a ( type) radiant system. 2 Ice melt system is a ( type) system with (type) automatic controls to shut of system at xx F. 3 Roof deicing system is a ( type) system with (type) automatic controls to shut of system at xx F. 4. Freeze protection system is a ( type) system with (type) automatic controls to shut of system at xx F. | System details on drawing M-xx, M-xx, and Schedules or specifications on M-xx indicate setpoints | COMPLIES or N/A
C408 ASHRAE 4.2.5 | MAINTENANCE INFORMATION AND BUILDING SYSTEM COMMISSIONING | Provisions for maintenance information and commissioning of, or functional testing for, building systems. | Building systems shall be commissioned and completed in accordance with Section C408 | Describe reporting and responsibility | Report to be submitted by ( responsible party) | COMPLIES or N/A
Black Text - Compliance Information DO NOT EDIT
Red Text - New Compliance Requirements for 2025 NYCECC
Blue Text - Proposed Values to be input by Applicant

## Com.ECC - SWH
2025 NYCECC Tabular Analysis Commercial Building - Envelope
Energy Code Scope of Work - Climate Zone 4
Job # | xxxxxxxxx | DOBNOW Job Type: | e.g. NB, Alt-CO, Alteration |  | DOB NOW Work Type: | e.g. I-1/GC- , P-2/ MS, PL
Filing Scope of Work |  | Enter PW-1 Scope of Work. Provide additional information and detailed description of Energy Code related work included in this Tabular Analysis
Note for ALTERATION job application: For each altered element where ALTERATION-specific exception/allowance is applied, edit the applicable row in the Proposed Design Value to cite the code section and to report the Supporting Documentation location. For examples of ALTERATION-specific exceptions/allowances, refer to 101.2.5 and C503.1
Does the alteration Scope of Work constitute: A Change of Use to the Building or any of the Spaces __________ or A major modification to the HVAC System(s).___________ For all ALTERATION job applications where the proposed scope of alteration work is limited to partial areas of the existing buildings and/or conditions, please provide a detailed description of the Area of Work, Proposed scope of work and itemize the specific altered elements in the tabular format below.
Professional Statement: "To the best of my knowledge, belief and professional judgment, this application is in compliance with the 2025 New York City Energy Conservation Code | [5 empty] | Chapter C4 or NYC ASHRAE 90.1 "
NYCECC Citation | Provision | Item Description | Code Prescriptive Value (ECC) |  | Proposed Design Value | Supporting Documentation | Code Compliance
SERVICE HOT WATER COMPONENTS
C404.2 ASHRAE 7.4.1 | MIN. EFFICIENCY REQUIREMENTS | Water-heating equipment and hot water storage tanks shall meet the requirements of Table C404.2. The efficiency shall be verified through data furnished by the manufacturer of the equipment or through certification under an approved certification program. Water-heating equipment intended to be used to provide space heating shall meet the applicable provisions of Table C404.2. (Tables in this code are intended to be a restatement of the legally binding provisions found in Title 10 CFR Part 431 included here as a convenience). For equipment not listed below , refer to Table C404.2 Where Code required ASHRAE values are applied, refer to Section 7.4.1 and Table 7.4-1 and indicate both code require and proposed efficiencies.
Table 404.2 Table 7.4-1 | EQUIPMENT TYPE | SIZE CATEGORY , RATING CONDITION | DRAW PATTERN | PERFORMANCE REQUIRED | PERFORMANCE PROPOSED
| Electric table-top water heaters | ≤ 12 kW, ≥ 20 gal ≤ 120 gal | Very small | UEF ≥ 0.6323 – (0.0058 × Vr) | UEF ≥ 0.6323 – (0.0058 × Vr) | Drawing details on P-xx, EN-xx Specifications on drawing P-xx | COMPLIES or N/A
|  |  | Low | UEF ≥ 0.9188 – (0.0031 × Vr) | UEF ≥ 0.9188 – (0.0031 × Vr) | Drawing details on P-xx, EN-xx Specifications on drawing P-xx | COMPLIES or N/A
|  |  | Medium | UEF ≥ 0.9577 – (0.0023 × Vr) | UEF ≥ 0.9577 – (0.0023 × Vr) | Drawing details on P-xx, EN-xx Specifications on drawing P-xx | COMPLIES or N/A
|  |  | High | UEF ≥ 0.9884 – (0.0016 × Vr) | UEF ≥ 0.9884 – (0.0016 × Vr) | Drawing details on P-xx, EN-xx Specifications on drawing P-xx | COMPLIES or N/A
| Electric storage water heaters resistance and heat pump | ≤ 12 kW ,≥ 20 gal ≤ 55 gal | Very small | UEF ≥ 0.8808 – (0.0008 × Vr) | UEF ≥ 0.8808 – (0.0008 × Vr) | Drawing details on P-xx, EN-xx Specifications on drawing P-xx | COMPLIES or N/A
|  |  | Low | UEF ≥ 0.9254 – (0.0003 × Vr) | UEF ≥ 0.9254 – (0.0003 × Vr) | Drawing details on P-xx, EN-xx Specifications on drawing P-xx | COMPLIES or N/A
|  |  | Medium | UEF ≥ 0.9307 – (0.0002 × Vr) | UEF ≥ 0.9307 – (0.0002 × Vr) | Drawing details on P-xx, EN-xx Specifications on drawing P-xx | COMPLIES or N/A
|  |  | High | UEF ≥ 0.9349 – (0.0001 × Vr) | UEF ≥ 0.9349 – (0.0001 × Vr) | Drawing details on P-xx, EN-xx Specifications on drawing P-xx | COMPLIES or N/A
|  |  | Very small | UEF ≥ 1.9236 – (0.0011 × Vr) | UEF ≥ 1.9236 – (0.0011 × Vr) | Drawing details on P-xx, EN-xx Specifications on drawing P-xx | COMPLIES or N/A
|  | ≤ 12 kW, > 55 gal ≤120 gal | Low | UEF ≥ 2.0440 – (0.0011 × Vr) | UEF ≥ 2.0440 – (0.0011 × Vr)
|  |  | Medium | UEF ≥ 2.1171 – (0.0011 × Vr) | UEF ≥ 2.1171 – (0.0011 × Vr)
|  |  | High | UEF ≥ 2.2418 – (0.0011 × Vr) | UEF ≥ 2.2418 – (0.0011 × Vr)
| Electric storage water heaters | > 12 kW | — | (0.3 + 27/Vm), %/h | (0.3 + 27/Vm), %/h | Drawing details on P-xx, EN-xx Specifications on drawing P-xx | COMPLIES or N/A
| Grid enabled water heaters | > 75 gal | Very small | UEF ≥ 1.0136 – (0.0028 × Vr) | UEF ≥ 1.0136 – (0.0028 × Vr) | Drawing details on P-xx, EN-xx Specifications on drawing P-xx | COMPLIES or N/A
|  |  | Low | UEF ≥ 0.9984 – (0.0014 × Vr) | UEF ≥ 0.9984 – (0.0014 × Vr)
|  |  | Medium | UEF ≥ 0.9853 – (0.0010 × Vr) | UEF ≥ 0.9853 – (0.0010 × Vr)
|  |  | High | UEF ≥ 0.9720 – (0.0007 × Vr) | UEF ≥ 0.9720 – (0.0007 × Vr)
| Electric instantaneous water heaters | ≤ 12 kW < 2 gal | Very small | UEF ≥ 0.91 | UEF ≥ 0.91 | Drawing details on P-xx, EN-xx Specifications on drawing P-xx | COMPLIES or N/A
|  |  | Low | UEF ≥ 0.91 | UEF ≥ 0.91
|  |  | Medium | UEF ≥ 0.91 | UEF ≥ 0.91
|  |  | High | UEF ≥ 0.92 | UEF ≥ 0.92
|  | > 12 kW & ≤ 58.6 kW,≤ 2 gal & ≤180ºF i | All | UEF ≥ 0.80 | UEF ≥ 0.80 | Drawing details on P-xx, EN-xx Specifications on drawing P-xx | COMPLIES or N/A
| Gas storage water heaters | ≤ 75,000 Btu/h, ≥20 gal & ≤ 55 ga | Very small | UEF ≥ 0.3456 – (0.0020 × Vr) | UEF ≥ 0.3456 – (0.0020 × Vr) | Drawing details on P-xx, EN-xx Specifications on drawing P-xx | COMPLIES or N/A
|  |  | Low | UEF ≥ 0.5982 – (0.0019 × Vr) | UEF ≥ 0.5982 – (0.0019 × Vr)
|  |  | Medium | UEF ≥ 0.6483 – (0.0017 × Vr) | UEF ≥ 0.6483 – (0.0017 × Vr)
|  |  | High | UEF ≥ 0.6920 – (0.0013 × Vr) | UEF ≥ 0.6920 – (0.0013 × Vr)
|  | ≤ 75,000 Btu/h > 55 gal & ≤ 100 gal | Very small | UEF ≥ 0.6470 – (0.0006 × Vr) | UEF ≥ 0.6470 – (0.0006 × Vr) | Drawing details on P-xx, EN-xx Specifications on drawing P-xx | COMPLIES or N/A
|  |  | Low | UEF ≥ 0.7689 – (0.0005 × Vr) | UEF ≥ 0.7689 – (0.0005 × Vr)
|  |  | Medium | UEF ≥ 0.7897 – (0.0004 × Vr) | UEF ≥ 0.7897 – (0.0004 × Vr)
|  |  | High | UEF ≥ 0.8072 – (0.0003 × Vr) | UEF ≥ 0.8072 – (0.0003 × Vr)
|  | > 75,000 Btu/h | Very small | UEF ≥ 0.2674 – (0.0009 × Vr) | UEF ≥ 0.2674 – (0.0009 × Vr) | Drawing details on P-xx, EN-xx Specifications on drawing P-xx | COMPLIES or N/A
|  | ≤ 105,000 Btu/h | Low | UEF ≥ 0.5362 – (0.0012 × Vr) | UEF ≥ 0.5362 – (0.0012 × Vr)
|  | ≤ 120 gal & ≤180ºF | Medium | UEF ≥ 0.6002 – (0.0011 × Vr) | UEF ≥ 0.6002 – (0.0011 × Vr)
|  |  | High | UEF ≥ 0.6597 – (0.0009 × Vr) | UEF ≥ 0.6597 – (0.0009 × Vr)
|  | > 105,000 Btu/hk | — | 80% Et | 80% Et | Drawing details on P-xx,EN-xx Specifications on drawing P-xx | COMPLIES or N/A
|  |  |  | SL ≤ Q / (800 + 110√V), Btu/ h | SL ≤ Q / (800 + 110√V), Btu/ h
See Table C404.2, footnotes a-m for specific requirements, calculations and definitions
C404.2.1 7.5.3 | High-input service water-heating systems | Gas-fired water heaters installed in new buildings where the total input capacity provided by high-capacity gas-fired water heaters is 1,000,000 Btu/h (293 kW) or greater shall comply with either or both of the following requirements:. | 1. Where a singular piece of a high-capacity gas-fired water heater is installed, the water heater shall have a thermal efficiency, Et, of not less than 92 percent. 2. Where multiple pieces of high-capacity gas-fired water heaters are connected to the same system, the combined input-capacity-weighted average thermal efficiency, Et, shall be not less than 90 percent, and a minimum of 30 percent shall have an Et of not less than 92 percent., unless allowed per exceptions C404.2.1( 1-3). |  | 1. The proposed high-capacity gas-fired water heater has a thermal efficiency, Et, of not less than xx percent Y/N . 2. Multiple high-capacity gas-fired water heaters are connected to the same system and the combined input-capacity-weighted average thermal efficiency, Et, is not less than xx percent, and a minimum of 30 percent shall have an Et of not less than xx percent Y/N | Drawing details on P-xx, EN-xx Specifications on drawing P-xx | COMPLIES or N/A
C404.3 7.4.6 | Heat traps for hot water storage tanks | Storage tank-type water heaters and hot water storage tanks shall be provided with integral heat traps | Storage tank-type water heaters and hot water storage tanks that have vertical water pipes connecting to the inlet and outlet of the tank shall be provided with integral heat traps at those inlets and outlets or shall have pipe configured heat traps in the piping connected to those inlets and outlet .Solar water-heating system circulation loops shall not be required to have heat traps. |  | Storage tank-type water heaters and hot water storage tanks that have vertical water pipes connecting to the inlet and outlet of the tank are provided with integral heat traps at those inlets and outlets. Y/N | Drawing details on P-xx, EN-xx Specifications on drawing P-xx | COMPLIES or N/A
C404.4 7.4.3 | Service water heating system piping insulation. | Service water heating system piping shall be surrounded by uncompressed insulation. The wall thickness of the insulation shall be not less than the thickness shown in Table C404.4.1. Where the insulation thermal conductivity is not within the range in the table, Equation 4-8 shall be used. |  |  |  | Drawing details on P-xx, EN-xx Specifications on drawing P-xx | COMPLIES or N/A | z
Table 404.4.1 or Table 7.4-2 (exposed values in italics) |  | INSULATION THERMAL CONDUCTIVITY |  | NOMINAL PIPE OR TUBE SIZE (inches) |  |  |  | z
| SHW TEMPERATURE RANGE | Conductivity (Btu × in/h × ft2 × °F) | Mean Rating Temp. (°F) | < 1 1/2 | 1 ½ to < 4 | 4 to > 8 |  | z
|  |  |  | Insulation Thickness (inches) |  |  |  | z
| 105°F to 140°F | 0.22 to 0.28 | 100 | 1.0 | 1.5 | 1.5 or 2.0 |  | z
| > 140°F to 200°F | 0.25 to 0.29 | 125 | 1.0 or 1.5 | 2.0 or 2.5 | 2.0 or 2.5
| > 200°F | 0.27 to 0.30 | 150 | 1.5 or 2.5 | 2.5 or 3.0 | 3.0
C404.5 | Heated water supply piping | Heated water supply piping shall be in accordance with Section C404.5.1 or C404.5.2. | The flow rate through 1/4-inch (6.4 mm) piping shall be not greater than 0.5 gpm (1.9 L/m). The flow rate through 5/16 inch (7.9 mm) piping shall be not greater than 1 gpm (3.8 L/m). The flow rate through 3/8-inch (9.5 mm) piping shall be not greater than 1.5 gpm (5.7 L/m). 5.1 The maximum allowable piping length from the nearest source of heated water to the termination of the fixture supply pipe shall use the largest pipe size and be determined per Table C404.5.1 5.2 Maximum allowable pipe volume in the piping shall be calculated in accordance with Section C404.5.2 as determined C404.5.2.1 and Table C404.5.2.1 |  | 5.1 'Supply Piping is determined by the maximum allowable pipe length method where nominal pipe size = xx volume /ft. = xx , and maximum pipe length = xx '5.2 'Supply Piping is determined by the maximum allowable pipe volume method where nominal pipe size = xx, Copper type L = xx , and Copper Type K = xx | Drawing details on P-xx, EN-xx Specifications on drawing P-xx | COMPLIES or N/A
C404.6 7.4.4 | Heated-water circulating and temperature maintenance systems | Heated-water circulation systems shall be in accordance with C404.6.1. Heat trace temperature systems shall be in accordance with C404.6.2. Controls for hot water storage shall be in accordance with C404.6.3. See 7.4.4 for NYC ASHRAE compliance requirements | 6.1 Heated-water circulation systems shall be provided with a circulation pump with a dedicated return pipe. Controls shall be configured to automatically turn off the pump when the water in the circulation loop is at the desired temperature and when there is not a demand for hot water. 6.2 Heat trace systems. Electric heat trace systems shall comply with IEEE 515.1. Controls for such systems shall be able to automatically adjust the energy input to the heat tracing to maintain the desired water temperature in the piping... 6.3 Controls for hot water storage. The controls on pumps that circulate water between a water heater and a heated-water storage tank shall limit operation of the pump from heating cycle startup to not greater than 5 minutes after the end of the cycle. |  | 6.1 Heated-water circulation system is provided with a circulation pump, dedicated return pipe and controls as required by C404.6.1. Y/N 6.2 Electric heat trace systems meet the requirements of IEEE 515.1. in accordance with C404.6.2. Y/N 6.3 Hot water storage controls limit operation of the pump from heating cycle startup to not greater than 5 minutes after the end of the cycle. Y/N | Drawing details on P-xx, EN-xx Specifications on drawing P-xx | COMPLIES or N/A
C404.7 | Drain water heat recovery units | Drain water heat recovery units shall comply with CSA B55.2. | Potable water-side pressure loss shall be less than 10 psi (69 kPa) at maximum design flow. For Group R occupancies, the efficiency of drain water heat recovery unit efficiency shall be in accordance with CSA B55.1. |  | Potable water-side pressure loss is proposed to be less than xx psi (xx kPa) at maximum design flow. Y/N Project contains Group R occupancies, where the efficiency of drain water heat recovery unit efficiency shall be in accordance with CSA B55.1. Y/N | Drawing details on P-xx, EN-xx Specifications on drawing P-xx | COMPLIES or N/A
C404.8 7.4.7 | Demand responsive water heating. | Where applicable, Demand response shall be provided. | Electric storage water heaters with a rated water storage volume of 40 gallons (150L) to 120 gallons (450L) and a nameplate input rating equal to or less than 12kW shall be provided with demand responsive controls in accordance with AHRI Standard 1430 or ANSI/CTA-2045-B Level 1 |  | Electric storage water heaters are rated with water storage volume of xx gallons and have a nameplate input rating equal to or less than xx kW .. All units are provided with demand responsive controls in accordance with AHRI Standard 1430 or ANSI/CTA-2045-B Level 1 | Schedules on P-xx, EN-xx Specifications on drawing P-xx | COMPLIES or N/A
C404.9 7.4.5 | Energy consumption of pools and permanent spas. | The energy consumption of pools and permanent spas shall be controlled by the requirements in Sections C404.9.1 through C404.9.3 | 9.1 The electric power to all heaters shall be controlled by an on-off switch that is an integral part of the heater… 9.2 Time switches or control methods that can turn off and on heaters and pump motors according to a preset schedule shall be installed for heaters and pump motors. 9.3 Outdoor heated pools and outdoor permanent spas shall be provided with a vapor-retardant cover or other approved vapor-retardant means |  | 9.1 Electric power to all heaters is controlled by an on-off switch that is an integral part of the heater… Y/N 9.2 Time switches or control methods turn on/off heaters and pump motors according to a preset schedule Y/N 9.3 Outdoor heated pools and outdoor permanent are provided with a vapor-retardant cover or other approved vapor-retardant means Y/N | Drawing details on P-xx, EN-xx Specifications on drawing P-xx | COMPLIES or N/A
Black Text - Compliance Information DO NOT EDIT
Red Text - New Compliance Requirements for 2025 NYCECC
Blue Text - Proposed Values to be input by Applicant

## Com.ECC - Lighting
2025 NYCECC Tabular Analysis Commercial Building - Envelope
Energy Code Scope of Work - Climate Zone 4
Job # | xxxxxxxxx | DOBNOW Job Type: | e.g. NB, Alt-CO, Alteration | DOB NOW Work Type: | e.g. I-1/GC- , P-2/ MS, PL
Filing Scope of Work |  | Enter PW-1 Scope of Work. Provide additional information and detailed description of Energy Code related work included in this Tabular Analysis
Note for ALTERATION job application: For each altered element where ALTERATION-specific exception/allowance is applied, edit the applicable row in the Proposed Design Value to cite the code section and to report the Supporting Documentation location. For examples of ALTERATION-specific exceptions/allowances, refer to 101.2.5 and C503.1
Does the alteration Scope of Work constitute: A Change of Use to the Building or any of the Spaces __________ or A major modification to the HVAC System(s).___________ For all ALTERATION job applications where the proposed scope of alteration work is limited to partial areas of the existing buildings and/or conditions, please provide a detailed description of the Area of Work, Proposed scope of work and itemize the specific altered elements in the tabular format below.
Professional Statement: "To the best of my knowledge, belief and professional judgment, this application is in compliance with the 2025 New York City Energy Conservation Code |  |  |  |  | Chapter C4 or NYC ASHRAE 90.1 "
NYCECC Citation | Provision | Item Description | Code Prescriptive Value (ECC) | Proposed Design Value | Supporting Documentation | Code Compliance
ELECTRICAL POWER & LIGHTING SYSTEMS
| Lighting Controls | ...Lighting systems powered through the energy service for the building and building site lighting for which the building owner is responsible shall be provided with controls that comply with Sections C405.2.1 through C405.2.8. except: 1. Spaces where an automatic shutoff could endanger occupant safety or security., 2. Interior exit stairways, interior exit ramps and exit passageways (as defined by the NYC Building Code)., 3. Emergency lighting that is automatically off during normal operations., 4. Emergency lighting required by the New York City Building Code in exit access components that are not provided with fire alarm systems., 5. Up to 0.02 watts per square foot (0.22 W/m2) of lighting in exit access components that are provided with fire alarm systems. Where ASHRAE values are applied , see Section 9.1 and Table 9.2.2.1, Table 9.2.2.2, Table 9.3.2, Table 9.4.2-2, Table 9.5.1 or Table 9.5.2.1-1 & Table 9.5.2.1-2, Table 9.5.2.2 and Table 9.5.2.3
C405.2.1 9.4.1.1 Tables 9.5.2.1 | Occupancy Sensor Controls | Interior general lighting occupancy controls | Occupant sensor controls shall be installed to control lights in all space types defined in C405.2.1 or 9.4.1.1 | Occupant sensor controls are provided in all spaces, including all corridors, stairways, lobbies, offices, amenity spaces, etc. per Reflected Ceiling Plans. Areas that do not have occupancy control include ( describe areas & exceptions, where applicable) | Plans, schedules and specifications on RCP-xx | COMPLIES or Not Applicable
C405.2.1.1 C405.2.1.2 C405.2.1.3 C405.2.1.4 C405.2.1.5 9.4.1.1 | Occupant sensor control function | Controls in warehouses storage areas shall comply with Section C405.2.1.2. Controls in open plan office areas, cafeteria dining areas, and fast food dining areas, 300 square feet (28 m2) or greater in area shall comply with Section C405.2.1.3. Controls in corridors shall comply with Section C405.2.1.4. Control function for egress shall comply with Section C405.2.1.5 | Occupant sensor controls for all other spaces specified in Section C405.2.1 shall comply with the following: 1. They shall automatically turn off lights within 15 minutes after all occupants have left the space. 2. They shall be manual-on or controlled to automatically turn on the lighting to not more than 50-percent power of full power. 3. They shall incorporate a manual control to allow occupants to turn off light | Occupancy Controls provided for: . Classrooms or Offices Y/N Amenity Areas Y/N Restrooms & Storage Areas Y/N Warehouse Storage Areas Y/N Offices & Dining Areas Y/N Corridors & Stairs Y/N Means of Egress Y/N | Plans indicating locations of sensors and specifications on drawing RCP-xx | COMPLIES or N/A
C405.2.2.1 9.4.1.1 | Time-Switch controls | Each area of the building that is not provided with occupant sensor controls complying with Section C405.2.1.1 shall be provided with time-switch controls complying with Section C405.2.2.1 | Time-switch controls shall comply with all of the following: 1. Programmed to automatically turn off lights when the space is scheduled to be unoccupied. 2. Have a minimum 7-day clock. 3. Be set for seven different day types per week. 4. Incorporate an automatic holiday “shutoff” feature, which turns off all controlled lighting loads for not fewer than 24 hours and then resumes normally scheduled operations. 5. Have program backup capabilities, which prevent the loss of program and time settings for not fewer than 10 hours, if power is interrupted. 6. Include an override switch per 6.1 through 6.3 7. All other controls are programmed by default to a schedule that turns off lights not less than 12 hours per day. | Time Switches provided for: . Amenity Areas Y/N Mercantile Areas Y/N Storage Areas Y/N Equipment Areas Y/N | Plans indicating locations of switches and specifications on drawing RCP-xx | COMPLIES or N/A
C405.2.3 9.4.1.1 | Dimming control function | Dimming controls complying with Section C405.2.3.1 are required for general lighting in the following space types: | 1. Classrooms/lecture hall/training rooms. 2. Conference/meeting rooms. 3. Dining for bar/lounge or family dining. 4. Gymnasiums/fitness centers. 5. Health care facility imaging rooms, exam rooms, nurseries or nurses’ stations. 6. Laboratories. 7. Library reading rooms. 8. Lobbies. 9. Lounge/break rooms. 10. Offices. 11. Spaces not provided with occupant sensor controls complying with Section C405.2.1.1. | Dimming Controls provided for: . Classrooms Y/N Meeting Rooms Y/N Dining Areas Y/N Fitness Areas Y/N Healthcare Facilities Y/N Laboratory Areas Y/N Library Reading Areas Y/N Lobbies Y/N Lounge/Breakrooms Y/N Offices Y/N | Plans indicating locations of dimming controls on RCP-xx and schedules/specifications on drawing RCP-xx | COMPLIES or N/A
C405.2.4 Figures C405.2.4 9.4.1.1 | Daylight responsive controls & function | Daylight responsive controls complying with Section C405.2.4.1 shall be provided to control the general lighting within daylight zones in the following spaces: | 1. Spaces with a total of more than 75 watts of general lighting within primary sidelight daylight zones complying with Section C405.2.4.2. 2. Spaces with a total of more than 150 watts of general lighting within sidelit daylight zones complying with Section C405.2.4.2. 3. Spaces with a total of more than 75 watts of general lighting within toplit daylight zones complying with Section C405.2.4.3. | Daylight Zones are indicated at: describe areas that have daylight zones including location in building. Where applicable describe exceptions Per C405.2.4, (exceptions) | Plans indicating locations of zones with notes regarding controls on drawing RCP-xx | COMPLIES or N/A
C405.2.5 9.4.1.3 | Specific Applications controls | Specific application controls shall be provided for the following: | 1. Lighting shall be controlled by an occupant sensor complying with Section C405.2.1.1 or a time-switch control complying with Section C405.2.2.1., 1.1.through 1.4 2. Lighting for nonvisual applications, such as plant growth and food warming. 3. Task lighting for medical and dental use 4. Lighting integrated into range hoods and exhaust fans shall be controlled independently of fans. . Compliance with NYC ASHRAE shall meet the requirments of 9.4.1.3 | Application controls provided for: describe areas that have specific application controls including location in building. | Plans indicating locations of zones with notes regarding controls on drawing RCP-xx | COMPLIES or N/A
C405.2.7 9.4.1.4 | Exterior Lighting Controls | Exterior lighting systems shall be provided with controls that comply with Sections C405.2.7.1 through C405.2.7.3 or 9.4.1.4 | 7.1. Daylight Shutoff -Lights shall be automatically turned off when daylight is present and satisfies the lighting needs. 7.2 Facade & Landscape Lighting - Building facade and landscape lighting shall shut off, when daylight is present 7.3. Lighting Setback - Lighting shall be controlled so that lighting is automatically reduced by not less than 50 percent per 1.1 through 1.3 or per C405.2.7.2. (2) . or as specifically defined in ASHRAE 9.4.1.4 | . Shutoff Controls provided for: Daylight Y/N Facades Y/N Landscape lighting Y/N Setback for 12mid-6am Y/N One hour after closing Y/N for No activity Y/N Exterior Parking Areas Y/N | Plans indicating locations of dimming controls on RCP-xx and schedules/specifications on drawing RCP-xx | COMPLIES or N/A
C405.2.8 9.4.1.5.1 | Demand response lighting controls | Interior general lighting in group B, E, M, and S occupancies shall have demand responsive controls complying with C405.2.8.1 or 9.4.1.5.1 in not less than 75 percent of the interior floor area. | Demand responsive controls for lighting shall be capable of the following: 1. Automatically reducing the output of controlled lighting to 80 percent upon receipt of a demand response signal. 2. Automatically reducing the output of controlled lighting to 80 percent or less of the high-end trim setpoint upon receipt of a demand response signal. 3. Dimming controlled lights over a period of not longer than 15 minutes to achieve their demand response setpoint. 4. Returning controlled lighting to its normal operational settings at the end of the demand response period. | Demand Response Controls provided for: describe type of demand response control and indicate areas in building where DRC will be activated. | Plans indicating locations of controls on RCP-xx and schedules/specifications on drawing RCP-xx | COMPLIES or N/A
C405.2.9 9.4.1.2 | Interior Parking Area lighting controls | Interior parking area lighting shall be controlled by an occupant sensor complying with Section C405.2.1.1 or a time-switch control complying with Section C405.2.2.1. | Additional lighting controls shall be provided as follows: 1. Lighting power shall be automatically reduced by not less than 30 percent when there is no activity detected for 15 minutes unless exception applies 2. At vehicle entrances to buildings, lighting shall be separately controlled to automatically reduce lighting power by at least 50 percent from sunset to sunrise. 3. Luminaires within 20 feet (6096 mm) of perimeter wall openings or skylights shall automatically reduce in response to daylight by at least 50 percent. | Parking Area controls provided for: describe areas that have specific application controls including location in building. Where applicable describe exceptions Per C405.2.9, (exceptions) | Plans indicating locations of zones with notes regarding controls on drawing RCP-xx | COMPLIES or N/A
C405.2.10 9.4.1.3 9.4.3 | Sleeping unit and dwelling unit lighting and switched receptacle controls. | Sleeping units and dwelling units shall be provided with lighting controls and switched receptacles as specified in Sections C405.2.10.1 and C405.2.10.2 | Sleeping units and dwelling units in hotels & motels shall be provided with the following: 1. Not less than two 125V, 15- and 20-amp switched receptacles in each room, except for bathrooms, kitchens, foyers, hallways and closets. 2. Lighting controls shall turn off all lighting and switched receptacles within 15 minutes after all occupants have left the unit. Sleeping units in congregate living facilities shall be provided with the following: 1. Bathrooms shall have an occupant sensor control that automatically turns off lights within 15 minutes after all occupants have left the space. 2. Each unit shall have a manual control by the entrance that turns off all lighting and switched receptacles in the unit, except for lighting in bathrooms and kitchens. The manual control shall be marked to indicate its function | Occupancy Controls provided for: . Dwelling Units Y/N Hotel/Motel Y/N Congregate Facility Y/N | Plans indicating locations of controls on RCP-xx and schedules/specifications on drawing RCP-xx | COMPLIES or N/A
C405.3 Table 405.3.2(1) Table 405.3.2(2) Table 9.5.1 or Table 9.5.2.1 | Interior Lighting Power requirements | A building complies with this section where its total connected interior lighting power calculated under Section C405.3.1 is not greater than the interior lighting power allowance calculated under Section C405.3.2. Sleeping units and dwelling units shall comply with Section C405.3.3. | The total interior lighting power allowance (watts) for an entire building shall be determined according to Table C405.3.2(1) using the Building Area Method or Table C405.3.2(2) or 9.5.2.1 using the Space-by-Space Method. The interior lighting power allowance for projects that involve only portions of a building shall be determined according to Table C405.3.2(2) or 9.5.2.1 using the Space-by-Space Method. Buildings with unfinished spaces shall use the Space-by-Space Method. | Lighting Power Calculations have been determined using: describe method( building or space-by space) . Include a description of the major lighting space occupancies in building. | Lighting Plans, Fixture schedules including Space types, if applicable and Controls specifications on RCP-xx - RCP- xx | COMPLIES or N/A
C405.5 Table 405.5.2(1) Table 405.5.2(2)Table 405.5.2(3) Table 9.4.2-2 | Exterior Lighting Power requirements | The exterior lighting power allowance (watts) shall be calculated per C405.5.2 | 1. Lighting Zone (LZ) for the building shall be determined according to Table C405.5.2(1), 2. Each exterior area that is to be illuminated by lighting shall be determined by area type from Table C405.5.2(2). 3. Determine the total area or length of each area type and multiply by the value for the area type in Table C405.5.2(2) to determine the lighting watts allowed. 4. Total exterior lighting power allowance (watts) is the sum of the base site allowance determined according to Table C405.5.2(2), plus the watts from each area type. | Lighting Power Calculations have been determined using: Lighting Zone LZ -xx Base allowance Area: LPD Allowed LPD Proposed Describe xx w/ft2 xx w/ft2 Describe xx w/ft2 xx w/ft2 Describe xx w/ft2 xx w/ft2 Bldg. Total xx w/ft2 xx w/ft2 | Lighting Plans, Fixture schedules including Space types, if applicable and Controls specifications on RCP-xx - RCP- xx | COMPLIES or N/A
) | ELECTRICAL POWER SYSTEMS
C405.6 8.4.6 | Electrical metering | Electrical service within buildings shall comply with the following: | Each dwelling unit located in a Group R-2 building shall have a separate electrical meter. Each covered tenant space in a new building shall be equipped with a separate meter or sub-meter to measure the electrical consumption of such space when let or sublet. | Electrical meters provided for: xx meters for common space xx meters for dwelling units xx separate meters for tenant space | Plans indicating locations of meters on RCP-xx and schedules/specifications on drawing RCP-xx | COMPLIES or N/A
C405.7 8.4.4 | Electrical Transformers | Electrical Transformers | Low-voltage dry-type distribution electric transformers shall meet the minimum efficiency requirements of Table C405.7 | Transformer Type/ kVA : Efficiency Describe 9x.xx % Describe 9x.xx % | Plans and Schedules indicating Transformers on drawing XX-xx and specifications on RCP-xx | COMPLIES or N/A
C405.8 10.4.1 10.4.6 | Electric Motors | Electric Motors | Electric motors shall meet the minimum efficiency requirements of Tables C405.8(1) through C405.8(4) or 10.4.1 | HP/ Poles/ Open-Eclsd : Efficiency Describe xx.xx % Describe xx.xx % | Plans and Schedules indicating motors on dwg. XX-xx and specifications on RCP-xx | COMPLIES or N/A
C405.9 ASHRAE 90.4 | Data Centers & Computer Rooms | Requirements per ASHRAE 90.4 in addition to this code. | 9.1 'Transformers, UPS, motors and processing equipment in data centers shall comply with Section 8 of ASHRAE 90.4... 9.2 UPS in computer rooms shall comply with the requirements in Tables 8.5 and 8.6 of ASHRAE 90.4 … | Listed equipment shall comply by: describe method of compliance) | Plans and Schedules indicating equipment on dwg. XX-xx and specifications on RCP-xx | COMPLIES or N/A
C405.10 10.4.3 | Vertical and horizontal transportation systems & equipment | Elevators & Escalators | Vertical and horizontal transportation systems and equipment shall comply with section C405.10.1 through C405.10.3 or 10.4.3 | Listed equipment shall comply by: describe method of compliance) | Plans and Schedules indicating equipment on dwg. XX-xx and specifications on RCP-xx | COMPLIES or N/A
C405.12 10.4.9 | Commercial kitchen equipment | Kitchen equipment | Commercial kitchen equipment shall comply with the minimum efficiency requirements of Tables C405.12(1) through C405.12(5). | Listed equipment shall comply by: describe method of compliance) | Plans and Schedules indicating equipment on dwg. XX-xx and specifications on RCP-xx | COMPLIES or N/A
C405.13 8.4.2 | Automatic receptacle control function | Automatic receptacle control | Automatic receptacle controls shall be either split controlled receptacles with the top receptacle controlled, or be a controlled receptacle located within 12 inches (304.8 mm) of each uncontrolled receptacle. Controls strategy must comply with one of C405.13.1.2 ( 2.1, 2.2 or 2.3.) | Automatic receptacle equipment is split or spaced 12" away from uncontrolled receptacles and shall comply with control by providing: describe method of compliance | Plans and Schedules indicating equipment on dwg. XX-xx and specifications on RCP-xx | COMPLIES or N/A
C405.14 8.4.3 10.4.7 | Energy monitoring | Building Energy Monitoring for building 10,000 gross square feet or larger | New buildings .. shall be equipped to measure, monitor, record and report energy consumption in accordance with Sections C405.14.1 through C405.14.6 for load categories indicated in Table C405.14.2 and Sections C405.14.7 through C405.14.11 for end-use categories indicated in Table C405.14.8. | Monitoring of Energy use shall be provided by: List methods of compliance for each end use category or load. | Schedules indicating equipment on dwg. XX-xx and specifications on XX-xx | COMPLIES or N/A
C405.15 10.5.1 | Renewable energy systems | Buildings proposing renewable energy systems shall comply with Sections C405.15.1 through C405.15.4. or 10.5.1 | Buildings shall be provided with on-site renewable energy generation systems with a direct current (DC) nameplate power rating of not less than 0.75 watts per square foot (8.1 W/m2) multiplied by the sum of the gross conditioned floor area of all floors, not to exceed the combined gross conditioned floor area of the three largest floors or provide documentation verifying compliance with C405.15.2, C405.15.3 or C405.15.4 | Renewable Energy System shall be provided by: List system type & size with method of calculating compliance | Plans and Schedules indicating equipment on dwg. XX-xx and calculations and/or specifications on XX-xx | COMPLIES or N/A
C405.16 | Renewable energy Inverters | Buildings proposing renewable energy systems shall provide inverters that comply with C405.16 | Direct-current-to-alternating-current inverters serving on-site renewable energy systems or on-site electrical energy storage systems (ESS) shall be compliant with IEEE 1547 and UL 1741 | Renewable Energy System inverters shall be: List inverter type, manufacturer, model and indicate compliance with IEEE 1547 or UL1741 | Plans and Schedules indicating equipment on dwg. XX-xx and calculations and/or specifications on XX-xx | COMPLIES or N/A
Black Text - Compliance Information DO NOT EDIT
Red Text - New Compliance Requirements for 2025 NYCECC
Blue Text - Proposed Values to be input by Applicant

## Com.ECC - Add'l Eff
2025 NYCECC Tabular Analysis Commercial Building
Energy Code Scope of Work - Climate Zone 4
Job # | Axxxxxxxxxxx | DOBNOW JobType: | e.g. NB, Alt-CO, Alteration | DOB NOW Work Type: | e.g. I-1/GC- , P-2/ MS, PL
Filing Scope of Work |  | Enter PW-1 Scope of Work. Provide addititonal information and detailed description of Energy Code related work included in this Tabular Analysis
Note for ALTERATION job appliation: For each altered element where ALTERATION-specific exception/allowance is applied, edit the applicable row in the Proposed Design Value to cite the code section and to report the Supporting Documentation location. For examples of ALTERATION-specific exceptions/allowances, refer to 101.2.5 and C503.1
Does the alteratiopn Scope of Work constitute: A Change of Use to the Building or any of the Spaces __________ or A major modification to the HVAC System(s).___________ For all ALTERATION job applications where the proposed scope of alteration work is limited to partial areas of the existing buildings and/or conditions, please provide a detailed description of the Area of Work, Proposed scope of work and itemize the specific altered elements in the tabular format below.
Professional Satement: "To the best of my knowledge, belief and professional judgment, this application is in compliance with the 2025 New York City Energy Conservation Code Chapter C4." All requirements of this code, whether detailed herein or not, will be met during construction of the aforementioned project.
NYCECC Citation | Provision | Item Description | Code Prescriptive Value (ECC) | Proposed Design Value | Supporting Documentation | Code Compliance
ENVELOPE COMPONENTS
C406.4 | Enhanced digital lighting controls | Enhanced digital lighting controls | Interior lighting in the building shall have enhanced lighting controls that shall be located, scheduled and operated in accordance with Section C405.2.2 & C406.4 | Sample text: Office and lobby lighting provided as per requirements | Sample text: See RCPs, Lighting Schedule, LPD calculation, drawing A-XXX, EN-XXX
C406.5 | Dedicated outdoor air system | Dedicated outdoor air system with energy recovery | Buildings covered by Section C403.4 shall be equipped with an independent ventilation system designed to provide not less than the minimum 1OO percent outdoor air to each individual occupied space, as specified by the New York City Mechanical Code, and be equipped with an energy recovery system. | Sample text: MAU-1 provides 100% outside air provided to all occupied space and is equipped with an Energy Recovery device | Sample text: See Mechanical schedule, drawing M-XXX
C406.6 | Reduced energy use in service water heating | Reduced energy use in service water heating | At least 60% of the domestic hot water is provided by waste-heat recovery. Buildings shall be of the following types to use this compliance method: 1. Group R-I: Boarding houses, hotels or motels. 2. Group 1-2: Hospitals, psychiatric hospitals and nursing homes. 3. Group A-2: Restaurants and banquet halls or buildings containing food preparation areas. 4. Group F: Laundries. 5. Group R-2: Buildings with residential occupancies. 6. Group A-3: Health clubs and spas. | Sample text: 75% of DHW load provided by waste-heat from Cogeneration system *As a motel, Group R-1 building, this project complies to use this method. | Sample text: See Mechanical schedule, drawing M-XXX, EN-XXX
C406.7 | Enhanced envelope performance | Enhanced envelope performance | The thermal performance of the envelope shall demonatrate a minimum 15 % improvement compared to the requirements of Section C402.1.5. | Sample text: ComCheck displays 18% improvement beyond code minimum | Sample text: EN-100 sheet
C406.8 | Reduced air infiltration | Reduced air infiltration | Must show compliance through testing to no more than 0.25 cfm/ft2 of envelope area @ 75 PA and witnessed by the Progress Inspector as indicated on TR-8 inspection IIA7. | Building thermal envelope to be tested to no more than 0.4 cfm/ft2 of envelope area @ 75 PA and witnessed by the Progress Inspector as indicated on TR-8 inspection IIA7. | Sample text: EN-100 sheet
C408.2 | Mechanical renewable energy, and service water heating systems commissioning and completion requirements | Mechanical System Commissioning | Commissioning required on HVAC systems | Sample text: Commissioning will be performed on all HVAC systems Total building heating capacity: 1,585 MBH Total building cooling capacity: 1,400 MBH | Sample text: See total heating & cooling capacity calculation M-XXX, commissioning requirement note on EN-XXX